## Instructions
This model was developed as a collaboration between the SunSpec Alliance and The National Renewable Energy Labortories
Sun Spec Alliance
PVOMcost Proforma; a proforma cost modelling tool for PV industry operations and finance practitioners designing and budgetting PV O&M plans
Version: Beta 0.4
Revised: August 6th 2014
We are seeking feedback on the Beta PVOMcost Proforma tool during the monthof August 2014; send comments to TJKeating@sunspec.org
Contents | Type | Description
Inputs & Summary | User inputs | Primary input page with real-time model output. Select system type, enter basic system details, warranty switches for modelling service plans, etc. here
Commercial Rooftop Details | User inputs | [Optional] Modify detailed assumptions for Commercial Rooftop system type. Exercise caution when modifying default assumptions.
Residential Rooftop Details | User inputs | [Optional] Modify detailed assumptions for Residential Rooftop system type. Exercise caution when modifying default assumptions.
Ground-Mount Details | User inputs | [Optional] Modify detailed assumptions for Ground-Mount system type. Exercise caution when modifying default assumptions.
Labor Rates | User inputs | [Optional] Modify labor rate assumptions for each trade
Reports | Read-only | Additional model output summaries; read-only
Cash Flow | Read-only | Detailed line item cash flow output; read-only
Cleaning | Separate tool | Stand-alone modelling tool provided to help calculate optimal PV panel cleaning frequency. Not connected to model; must manully transfer result to appropriate details page
Legend
User input, hard-coded default value |  | Value
User input, calculated default value |  | Value
User input, drop down selection |  | Value
Input not applicable (user can over ride) |  | Value
Read-only output |  | Value
Note: Model is for informational purposes only
Please direct any comments for improvements or feedback to tjkeating@sunspec.org; This tool is provided in an open source format, please send improvements and derivative models to PVOMcostModel@sunspec.org
LICENSE AGREEMENT
THIS DOCUMENT AND THE INFORMATION CONTAINED HEREIN IS PROVIDED ON AN "AS IS" BASIS. THE SUNSPEC ALLIANCE DISCLAIMS ALL WARRANTIES,
EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE ANY OWNERSHIP
RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE.
THIS DOCUMENT MAY BE USED, COPIED, AND FURNISHED TO OTHERS, WITHOUT RESTRICTIONS OF ANY KIND, PROVIDED THAT THIS DOCUMENT ITSELF MAY NOT
BE MODIFIED IN ANYWAY, EXCEPT AS NEEDED BY THE SUNSPEC TECHNICAL COMMITTEE AND AS GOVERNED BY THE SUNSPEC IPR POLICY.
THE COMPLETE POLICY OF THE SUNSPEC ALLIANCE CAN BE FOUND AT WWW.SUNSPEC.ORG.

## Inputs & Summary
Inputs |  |  |  |  | Results
General Inputs
| Analysis Period (Project Life) | 20 | years (40 max) |  |  | First Year O&M Costs ($/year) | 4404.1281
| Discount Rate | 7% | % per annum |  |  | First Year Unit O&M Costs ($/kW/year) | 10.0094
| Inflation Rate | 2% | % per annum |  |  | Net Present Value O&M Costs (project life) | 137778.286
| Truck Rental Cost/ day | 100 |  |  |  | Net Present Value (project life) per Wp | 0.31313
| Working Hours/year | 2080
Note: Horz. axis range not yet dynamic
System Inputs
| Name of System | Hypothetical Roof-mount System #1
| Location | Denver, CO
| System Type | Grount-Mount Fixed Tilt (> 100kW)
| System Size (Wp DC) | 440000
| Energy Yield (kWh/kWp/year) | 1596
| Module Power (W STC) | 305
| Number of Modules | 1443
| Module Type/ Degradation | Mulit-crystal Silicon:0.64%/year
| Module Encapsulant | Ethyl Vinyl Acetate (EVA)
| Modules per String | 14
| Number of Strings | 103.0445
| Strings per Combiner Box | 6
| Number of Combiner Boxes | 18
| Combiner boxes per DC disconnect | 1
| Number of DC Disconnects | 18
| Inverter Type | String Inverter
| Inverter Replacement Cost/ Wp | 0.2
| Number of Inverters | 1
| Inverter Capacity (kWp) | 400
| Number of Transformers | 1
| Inverter Warranty (years) | 10
| PV Module Product Warranty (years) | 10
| Other equipment (EPC) Warranty (years) | 10
| Purchased monitoring contract (years) | 5 | Enter '0' if not applicable
| Ground Coverage Ratio (GCR) | 33%
| Site Area (acres) | 2.3153
| Modules/Row | 14
| Total Rows: | 103.0445
| Rows per Tracked Block:(ignore untracked) | 1
| Total Tracking Blocks:(ignore untracked) | 103.0445
| Foundations per row: (ignore rooftop) | 1
Environmental Conditions
Indicate "1" if condition applies to project, "0" if not applicable
| Snow | 0
| Pollen | 0
| Bird Populations | 0 |  | (reduce efficiency 2.67% for central, 0.18% for string inverter, Wang et al 2012)
| Sand/Dust | 0 |  | (reduce efficiency 1%/g, Wang et al 2012)
| Humid | 0
| Hot | 0
| High Wind | 0
| Hail | 0
| Salt Air | 0 |  | (reduce efficiency 1%/g, Wang et al 2012)
| Diesel Soot | 0 |  | (reduce efficiency 1%/g, Wang et al 2012)
| Industrial Emissions | 0
| Construction Site Nearby | 0
| High Insolation | 0 |  | (reduce availability 0.83%, Wang et al 2012)

## Commercial Rooftop Details
Commercial Rooftop (10kW - 1000kW)
Warning: You have selected Grount-Mount Fixed Tilt (> 100kW) on the Inputs and Summary page. Please go back and select Commercial System Type on Inputs & Summary Page
Inputs |  |  | Lifetime NPV by Service Type |  |  |  |  | Lifetime NPV by Component Type
Analysis Period (Project Life) | 20 |  | Service | Avg. Cost/Yr | NPV (Life) | % of Total |  | Component | Avg. Cost/Yr | NPV (Life) | % of Total
Discount Rate | 7% |  | Administrator | 357.8923 | 3512.8331 | 4.975% |  | Documents | 41.2976 | 418.8015 | 0.6169%
Inflation Rate | 2% |  | Cleaner | 1.3232 | 13.4183 | 0.01901% |  | Asset Management | 48.688 | 411.2613 | 0.6058%
Truck Rental Cost/ day | 100 |  | Inverter specialist | 1189.3299 | 8869.3238 | 12.56% |  | PV Array | 1282.5159 | 11093.4749 | 16.34%
Working Hours/year | 2080 |  | Inspector | 1948.3728 | 19745.9793 | 27.97% |  | Cleaning/Veg | 0 | 0 | 0%
System Size (Wp DC) | 440000 |  | Journeyman electrician | 3157.4071 | 22250.4158 | 31.51% |  | Electrical | 186.1509 | 1807.5625 | 2.663%
Energy Yield (kWh/kWp/year) | 1596 |  | PV module/array Specialist | 1257.5467 | 10753.8019 | 15.23% |  | Meter | 0 | 0 | 0%
Module Power (W STC) | 305 |  | Network/IT | 12.771 | 117.2266 | 0.166% |  | PV Module | 3203.7129 | 23554.7407 | 34.7%
Number of Modules | 1443 |  | Master electrician | 15.0804 | 117.1358 | 0.1659% |  | DC Wiring | 1569.9106 | 13236.3433 | 19.5%
Module Type/ Degradation | Mulit-crystal Silicon:0.64%/year |  | Mechanic | 554.1912 | 3741.5775 | 5.299% |  | Mechanical | 733.5631 | 7321.1813 | 10.78%
Module Encapsulant | Ethyl Vinyl Acetate (EVA) |  | Designer | 0 | 0 | 0% |  | AC Wiring | 105.4591 | 1069.6385 | 1.576%
Modules per String | 14 |  | Pest control | 146.1662 | 1482.2804 | 2.099% |  | Inverter | 1198.4514 | 8961.8262 | 13.2%
Number of Strings | 103.0445 |  | Roofing | 0 | 0 | 0% |  | Monitoring | 2.4704 | 12.7679 | 0.01881%
Strings per Combiner Box | 6 |  | Structural engineer | 0 | 0 | 0% |  | Total | 8372.2199 | 67887.598 | 100%
Number of Combiner Boxes | 18 |  | Mower/Trimmer | 0 | 0 | 0%
Combiner boxes per DC disconnect | 1 |  | Utilities locator | 0 | 0 | 0%
Number of DC Disconnects | 18 |  | Total | 8640.0808 | 70603.9923 | 100%
Inverter Type | String Inverter
Inverter Warranty (years) | 10
Number of Inverters | 1
Inverter Capacity (kWp) | 400
Number of Transformers | 1
Detailed Measures | [21 empty] | Annual Cash Flow
Activity Description | Activity Type | Component Type | Applicable ? (1= yes, 0 = no) | Covered by Warranty - Materials (1=yes, 0=no) | Covered by Warranty - Labor (1=yes, 0=no) | Warranty or Service Package Type | Applicable Unit | Service Category | Labor Rate per Hour | Mean Interval (years) | Weibull or Lognormal Shape Factor | Type of Distribution | Approx. Number of Units | Labor hrs per unit | Material/ Other Cost per unit | Total Labor Cost | Total Matl and Other Cost | Total Cost for Measure | Notes | Reference | Average Annual Expense | NPV (Project Life) | % of Total NPV | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
Monitoring annual service package | Preventive | Asset Management | 1 | 1 | 1 | Monitoring | System | Administrator | 0 | 1 | 1 | interval | 1 | 0 | 50 | 0 | 50 | 50 |  |  | 48.688 | 411.2613 | 0.5825% | 0 | 0 | 0 | 0 | 0 | 56.3081 | 57.4343 | 58.583 | 59.7546 | 60.9497 | 62.1687 | 63.4121 | 64.6803 | 65.9739 | 67.2934 | 68.6393 | 70.0121 | 71.4123 | 72.8406 | 74.2974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter inspection | Preventive | Electrical | 1 | 1 | 1 | N/A | Inverter | Inspector | 25.1731 | 2 | 1 | interval | 1 | 1 | 0 | 25.1731 | 0 | 25.1731 |  |  | 15.7512 | 154.3843 | 0.2187% | 0 | 26.1901 | 0 | 27.2481 | 0 | 28.349 | 0 | 29.4943 | 0 | 30.6858 | 0 | 31.9255 | 0 | 33.2153 | 0 | 34.5572 | 0 | 35.9534 | 0 | 37.4059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrical labor mobilization | Preventive | Electrical | 1 | 1 | 1 | EPC | Site | Master electrician | 23.1971 | 2 | 1 | interval | 1 | 1 | 0 | 23.1971 | 0 | 23.1971 |  |  | 7.9737 | 54.4298 | 0.07709% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.4196 | 0 | 30.6081 | 0 | 31.8447 | 0 | 33.1312 | 0 | 34.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check position of disconnect switches and breakers. | Preventive | AC Wiring | 1 | 0 | 0 | N/A | Disconnect Box | Inspector | 25.1731 | 1 | 1 | interval | 18 | 0.08 | 0 | 36.2492 | 0 | 36.2492 |  |  | 44.9188 | 455.5245 | 0.6452% | 36.9742 | 37.7137 | 38.468 | 39.2373 | 40.0221 | 40.8225 | 41.639 | 42.4718 | 43.3212 | 44.1876 | 45.0714 | 45.9728 | 46.8922 | 47.8301 | 48.7867 | 49.7624 | 50.7577 | 51.7728 | 52.8083 | 53.8645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect electrical boxes for corrosion or intrusion of water or insects. Seal boxes if required. | Preventive | AC Wiring | 1 | 0 | 0 | N/A | Combiner Box | Inspector | 25.1731 | 1 | 1 | interval | 18 | 0.08 | 0 | 36.2492 | 0 | 36.2492 |  |  | 44.9188 | 455.5245 | 0.6452% | 36.9742 | 37.7137 | 38.468 | 39.2373 | 40.0221 | 40.8225 | 41.639 | 42.4718 | 43.3212 | 44.1876 | 45.0714 | 45.9728 | 46.8922 | 47.8301 | 48.7867 | 49.7624 | 50.7577 | 51.7728 | 52.8083 | 53.8645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check proper position of DC disconnect switches. | Preventive | DC Wiring | 1 | 0 | 0 | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 18 | 0.08 | 0 | 36.2492 | 0 | 36.2492 |  |  | 44.9188 | 455.5245 | 0.6452% | 36.9742 | 37.7137 | 38.468 | 39.2373 | 40.0221 | 40.8225 | 41.639 | 42.4718 | 43.3212 | 44.1876 | 45.0714 | 45.9728 | 46.8922 | 47.8301 | 48.7867 | 49.7624 | 50.7577 | 51.7728 | 52.8083 | 53.8645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DC circuit test & combiner box inspection | Preventive | Electrical | 1 | 0 | 0 | N/A | Combiner Box | PV module/array Specialist | 24.0385 | 1 | 1 | interval | 18 | 0.083333 | 0 | 36.0577 | 0 | 36.0577 |  |  | 44.6815 | 453.1176 | 0.6418% | 36.7788 | 37.5144 | 38.2647 | 39.03 | 39.8106 | 40.6068 | 41.419 | 42.2473 | 43.0923 | 43.9541 | 44.8332 | 45.7299 | 46.6445 | 47.5774 | 48.5289 | 49.4995 | 50.4895 | 51.4993 | 52.5292 | 53.5798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV module torque check & visual inspection | Preventive | Mechanical | 1 | 0 | 0 | N/A | Rail/ Fastener | PV module/array Specialist | 24.0385 | 5 | 1 | interval | 1648.7119 | 0.0083333 | 0 | 330.2708 | 0 | 330.2708 |  |  | 85.1255 | 752.5785 | 1.066% | 0 | 0 | 0 | 0 | 364.6457 | 0 | 0 | 0 | 0 | 402.5983 | 0 | 0 | 0 | 0 | 444.501 | 0 | 0 | 0 | 0 | 490.7651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV module electrical connection check | Preventive | Electrical | 1 | 0 | 0 | N/A | PV Module | PV module/array Specialist | 24.0385 | 5 | 1 | Interval | 1442.623 | 0.0041667 | 0 | 144.4935 | 0 | 144.4935 |  |  | 37.2424 | 329.2531 | 0.4663% | 0 | 0 | 0 | 0 | 159.5325 | 0 | 0 | 0 | 0 | 176.1368 | 0 | 0 | 0 | 0 | 194.4692 | 0 | 0 | 0 | 0 | 214.7097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Racking torque check & inspection | Preventive | Mechanical | 1 | 0 | 0 | N/A | Structure | Inspector | 25.1731 | 5 | 1 | interval | 103.0445 | 0.0083333 | 0 | 21.6162 | 0 | 21.6162 |  |  | 5.5715 | 49.2563 | 0.06976% | 0 | 0 | 0 | 0 | 23.8661 | 0 | 0 | 0 | 0 | 26.3501 | 0 | 0 | 0 | 0 | 29.0926 | 0 | 0 | 0 | 0 | 32.1206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check grounding hardware | Preventive | Electrical | 1 | 0 | 0 | N/A | Structure | Master electrician | 23.1971 | 1 | 1 | interval | 1 | 0.00055556 | 0 | 0.012887 | 0 | 0.012887 |  |  | 0.015969 | 0.16195 | 0.0002294% | 0.013145 | 0.013408 | 0.013676 | 0.01395 | 0.014229 | 0.014513 | 0.014803 | 0.0151 | 0.015402 | 0.01571 | 0.016024 | 0.016344 | 0.016671 | 0.017005 | 0.017345 | 0.017691 | 0.018045 | 0.018406 | 0.018774 | 0.01915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor available by email and phone 24x7x365 | Preventive | PV Array | 1 | 0 | 0 | N/A |  | Administrator | 16.6635 | 1 | 1 | interval | 1 | 12 | 0 | 199.9615 | 0 | 199.9615 |  |  | 247.7855 | 2512.8087 | 3.559% | 203.9608 | 208.04 | 212.2008 | 216.4448 | 220.7737 | 225.1892 | 229.693 | 234.2868 | 238.9725 | 243.752 | 248.627 | 253.5996 | 258.6716 | 263.845 | 269.1219 | 274.5043 | 279.9944 | 285.5943 | 291.3062 | 297.1323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Install software updates, inverter and other | Preventive | Electrical | 0 | 1 | 1 | EPC | NCU | Inverter specialist | 24.0385 | 5 | 1 | interval | 1 | 1 | 500 | 24.0385 | 500 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check central SCADA/network manager | Preventive | Electrical | 1 | 0 | 0 | N/A | NCU | Network/IT | 33.25 | 1 | 1 | interval | 1 | 0.25 | 0 | 8.3125 | 0 | 8.3125 |  |  | 10.3006 | 104.4587 | 0.148% | 8.4787 | 8.6483 | 8.8213 | 8.9977 | 9.1777 | 9.3612 | 9.5484 | 9.7394 | 9.9342 | 10.1329 | 10.3355 | 10.5423 | 10.7531 | 10.9682 | 11.1875 | 11.4113 | 11.6395 | 11.8723 | 12.1097 | 12.3519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Corrosion inpsection | Preventive | Mechanical | 1 | 0 | 0 | N/A | connection | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 259.3947 |  |  | 321.4331 | 3259.6732 | 4.617% | 264.5826 | 269.8742 | 275.2717 | 280.7772 | 286.3927 | 292.1206 | 297.963 | 303.9222 | 310.0007 | 316.2007 | 322.5247 | 328.9752 | 335.5547 | 342.2658 | 349.1111 | 356.0933 | 363.2152 | 370.4795 | 377.8891 | 385.4469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Galvanazation inspection | Preventive | Mechanical | 1 | 0 | 0 | N/A | connection | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 259.3947 |  |  | 321.4331 | 3259.6732 | 4.617% | 264.5826 | 269.8742 | 275.2717 | 280.7772 | 286.3927 | 292.1206 | 297.963 | 303.9222 | 310.0007 | 316.2007 | 322.5247 | 328.9752 | 335.5547 | 342.2658 | 349.1111 | 356.0933 | 363.2152 | 370.4795 | 377.8891 | 385.4469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Use infrared camera to inspect for hot spots; bypass diode failure | Preventive | PV Module | 1 | 0 | 0 | N/A | strings | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.15 | 0 | 389.0921 | 0 | 389.0921 |  |  | 482.1496 | 4889.5099 | 6.925% | 396.8739 | 404.8114 | 412.9076 | 421.1658 | 429.5891 | 438.1809 | 446.9445 | 455.8834 | 465.001 | 474.301 | 483.7871 | 493.4628 | 503.3321 | 513.3987 | 523.6667 | 534.14 | 544.8228 | 555.7193 | 566.8337 | 578.1703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-torque all electrical connections on AC side of system. | Preventive | AC Wiring | 1 | 0 | 0 | N/A |  | Journeyman electrician | 14.4231 | 1 | 1 | interval | 1 | 0.5 | 0 | 7.2115 | 0 | 7.2115 |  |  | 8.9363 | 90.6235 | 0.1284% | 7.3558 | 7.5029 | 7.6529 | 7.806 | 7.9621 | 8.1214 | 8.2838 | 8.4495 | 8.6185 | 8.7908 | 8.9666 | 9.146 | 9.3289 | 9.5155 | 9.7058 | 9.8999 | 10.0979 | 10.2999 | 10.5058 | 10.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test open circuit voltage or IV curve of series strings of modules | Preventive | PV Array | 1 | 0 | 0 | N/A | strings | PV module/array Specialist | 24.0385 | 1 | 1 | interval | 103.0445 | 0.15 | 0 | 371.5547 | 0 | 371.5547 |  |  | 460.4179 | 4669.1271 | 6.613% | 378.9858 | 386.5655 | 394.2968 | 402.1827 | 410.2264 | 418.4309 | 426.7995 | 435.3355 | 444.0422 | 452.9231 | 461.9815 | 471.2212 | 480.6456 | 490.2585 | 500.0637 | 510.0649 | 520.2662 | 530.6716 | 541.285 | 552.1107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AC disconnect box inspection | Preventive | Electrical | 1 | 0 | 0 | N/A | Disconnect Box | Inspector | 25.1731 | 1 | 1 | interval | 1 | 0.25 | 0 | 6.2933 | 0 | 6.2933 |  |  | 7.7984 | 79.0841 | 0.112% | 6.4191 | 6.5475 | 6.6785 | 6.812 | 6.9483 | 7.0872 | 7.229 | 7.3736 | 7.521 | 7.6715 | 7.8249 | 7.9814 | 8.141 | 8.3038 | 8.4699 | 8.6393 | 8.8121 | 8.9883 | 9.1681 | 9.3515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect cabling for signs of cracks, defects, pulling out of connections; overheating, arcing, short or open circuits, ground faults in wiring and condition of wire insulation and protective materials.. | Preventive | DC Wiring | 1 | 0 | 0 | N/A | strings | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 259.3947 |  |  | 321.4331 | 3259.6732 | 4.617% | 264.5826 | 269.8742 | 275.2717 | 280.7772 | 286.3927 | 292.1206 | 297.963 | 303.9222 | 310.0007 | 316.2007 | 322.5247 | 328.9752 | 335.5547 | 342.2658 | 349.1111 | 356.0933 | 363.2152 | 370.4795 | 377.8891 | 385.4469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test modules showing corrosion of ribbons to junction box | Preventive | PV Module | 0 | 0 | 0 | N/A | modules | Journeyman electrician | 14.4231 | 5 | 1 | interval | 1443 | 0.08 | 0 | 1665 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test output of modules that exhibit cracked glass, bubble formation oxidation of busbars, discoloration of busbars, or PV module hot spots (bypass diode failure) | Preventive | PV Module | 0 | 0 | 0 | N/A | modules | Journeyman electrician | 14.4231 | 5 | 1 | interval | 1443 | 0.08 | 0 | 1665 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exercise operation of all protection devices. | Preventive | AC Wiring | 1 | 0 | 0 | N/A |  | Journeyman electrician | 14.4231 | 1 | 1 | interval | 2 | 0.08 | 0 | 2.3077 | 0 | 2.3077 |  |  | 2.8596 | 28.9995 | 0.04107% | 2.3538 | 2.4009 | 2.4489 | 2.4979 | 2.5479 | 2.5988 | 2.6508 | 2.7038 | 2.7579 | 2.8131 | 2.8693 | 2.9267 | 2.9852 | 3.045 | 3.1059 | 3.168 | 3.2313 | 3.296 | 3.3619 | 3.4291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Array cleaning | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | Acre | Cleaner | 10.6779 | 0.25 | 1 | interval | 1 | 4 | 120 | 42.7115 | 120 | 0 | 2 gal fuel/acre @$4/gal + 500 gal H2O/acre @$0.40/gal |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
General Cleaning/Veg Mobilization | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | Site | Mower/Trimmer | 21.2308 | 1 | 1 | interval | 1 | 4 | 120 | 84.9231 | 120 | 0 | Other cost = water truckr rental |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation management (mowing, trimming) per acre | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | Acre | Mower/Trimmer | 21.2308 | 0.25 | 1 | interval | 2.3153 | 2 | 0 | 98.3103 | 0 | 0 | Other cost = 1 gal fuel/acre @ $4/gal + $10/acre mowing consumables |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Look for any signs of intrusion by pests such as insects and rodents. Remove any nests from electrical boxes (junction boxes, pull boxes, combiner boxes) or around the array. Use safe sanitation practices because pests may carry disease. | Preventive | DC Wiring | 1 | 0 | 0 | N/A |  | Pest control | 14.5865 | 1 | 1 | interval | 37 | 0.15 | 1 | 80.9553 | 37 | 117.9553 |  |  | 146.1662 | 1482.2804 | 2.099% | 120.3144 | 122.7207 | 125.1751 | 127.6786 | 130.2322 | 132.8368 | 135.4935 | 138.2034 | 140.9675 | 143.7868 | 146.6626 | 149.5958 | 152.5877 | 155.6395 | 158.7523 | 161.9273 | 165.1659 | 168.4692 | 171.8386 | 175.2754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Open each combiner box and check that no fuses have blown and that all electrical connections are tight. Use an infrared camera for identifying loose connections because they are warmer than good connections when passing current. | Preventive | DC Wiring | 1 | 0 | 0 | N/A | Combiner Box | Journeyman electrician | 14.4231 | 1 | 1 | interval | 18 | 0.15 | 0 | 38.9423 | 0 | 38.9423 |  |  | 48.256 | 489.367 | 0.6931% | 39.7212 | 40.5156 | 41.3259 | 42.1524 | 42.9955 | 43.8554 | 44.7325 | 45.6271 | 46.5397 | 47.4705 | 48.4199 | 49.3883 | 50.376 | 51.3835 | 52.4112 | 53.4594 | 54.5286 | 55.6192 | 56.7316 | 57.8662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-torque all electrical connections in combiner box. | Preventive | DC Wiring | 1 | 0 | 0 | N/A | Combiner Box | Journeyman electrician | 14.4231 | 1 | 1 | interval | 18 | 0.25 | 0 | 64.9038 | 0 | 64.9038 |  |  | 80.4266 | 815.6116 | 1.155% | 66.2019 | 67.526 | 68.8765 | 70.254 | 71.6591 | 73.0923 | 74.5541 | 76.0452 | 77.5661 | 79.1174 | 80.6998 | 82.3138 | 83.96 | 85.6392 | 87.352 | 89.0991 | 90.8811 | 92.6987 | 94.5526 | 96.4437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test system grounding with "megger" | Preventive | DC Wiring | 0 | 0 | 0 | N/A | strings | Master electrician | 23.1971 | 5 | 1 | interval | 103.0445 | 0.25 | 0 | 597.5838 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check Electrical connections (motor) | Preventive | Tracker | 1 | 0 | 0 | N/A | Motor | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.083333 | 0 | 216.1623 | 0 | 216.1623 |  |  | 267.8609 | 2716.3944 | 3.847% | 220.4855 | 224.8952 | 229.3931 | 233.981 | 238.6606 | 243.4338 | 248.3025 | 253.2685 | 258.3339 | 263.5006 | 268.7706 | 274.146 | 279.6289 | 285.2215 | 290.9259 | 296.7445 | 302.6793 | 308.7329 | 314.9076 | 321.2057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transformer/switchgear inspection | Preventive | Electrical | 1 | 0 | 0 | N/A | Transformer | Inspector | 25.1731 | 1 | 1 | interval | 1 | 2 | 0 | 50.3462 | 0 | 50.3462 |  |  | 62.3872 | 632.6729 | 0.8961% | 51.3531 | 52.3801 | 53.4277 | 54.4963 | 55.5862 | 56.6979 | 57.8319 | 58.9885 | 60.1683 | 61.3717 | 62.5991 | 63.8511 | 65.1281 | 66.4307 | 67.7593 | 69.1145 | 70.4968 | 71.9067 | 73.3448 | 74.8117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Clean (vacuum) dust from heat rejection fins | Preventive | Inverter | 1 | 0 | 0 | N/A | inverter | Cleaner | 10.6779 | 1 | 1 | interval | 1 | 0.1 | 0 | 1.0678 | 0 | 1.0678 |  |  | 1.3232 | 13.4183 | 0.01901% | 1.0891 | 1.1109 | 1.1331 | 1.1558 | 1.1789 | 1.2025 | 1.2266 | 1.2511 | 1.2761 | 1.3016 | 1.3277 | 1.3542 | 1.3813 | 1.4089 | 1.4371 | 1.4658 | 1.4952 | 1.5251 | 1.5556 | 1.5867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Performance test: measure incident light while observing temp and energy output. Calculate PV module efficiency as a function of temp and calculate BOS efficiency. Compare readings with diagnostic benchmark (original efficiency of system). | Preventive | Inverter | 0 | 0 |  | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 1 | 1 | 0 | 25.1731 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace any air filters on air-cooled equipment such as inverter. | Preventive | Inverter | 0 | 0 | 0 | N/A | inverter | Inverter specialist | 24.0385 | 1 | 1 | interval | 1 | 0.25 | 25 | 6.0096 | 25 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace transient voltage surge suppression devices | Preventive | Inverter | 0 | 0 | 0 | Inverter |  | Master electrician | 23.1971 | 5 | 1 | interval | 1 | 0.5 | 105 | 11.5986 | 105 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test overvoltage surge suppressors in inverter | Preventive | Inverter | 0 | 0 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 5 | 1 | interval | 1 | 0.1 | 0 | 2.4038 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter | Corrective | Inverter | 1 | 1 | 1 | Inverter | Inverter | Inverter specialist | 24.0385 | 10 | 1 | Weibull | 1 | 0 | 80300 | 0 | 80300 | 80300 | $300 flat fee |  | 1189.3017 | 8869.1204 | 12.56% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3323.4833 | 3067.3563 | 2830.9679 | 2612.797 | 2411.4397 | 2225.6001 | 2054.0823 | 1895.7828 | 1749.6827 | 1614.8419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace modules failing performance test or IR scan | Corrective | PV module | 1 | 1 | 1 | Module (Product) | modules | Journeyman electrician | 14.4231 | 50 | 2 | Weibull | 1443 | 0.15 | 244 | 3121.875 | 352092 | 355213.875 |  |  | 2721.5633 | 18665.2308 | 26.44% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3703.0078 | 4082.7036 | 4466.4984 | 4853.5741 | 5243.0891 | 5634.1822 | 6025.9748 | 6417.5748 | 6808.08 | 7196.5811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dispatch contractor in response to alarms, alerts, or contact by others | Corrective | PV Array | 1 | 1 | 1 | Monitoring |  | Administrator | 16.6635 | 1 | 1 | Interval | 1 | 1 | 4 | 16.6635 | 4 | 20.6635 |  |  | 20.1212 | 169.9616 | 0.2407% | 0 | 0 | 0 | 0 | 0 | 23.2704 | 23.7358 | 24.2105 | 24.6947 | 25.1886 | 25.6924 | 26.2063 | 26.7304 | 27.265 | 27.8103 | 28.3665 | 28.9338 | 29.5125 | 30.1028 | 30.7048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace MC connector lead to combiner box | Corrective | DC wiring | 1 | 1 | 1 | Module (Product) | modules | PV module/array Specialist | 24.0385 | 25 | 1 | Weibull | 1443 | 0.1 | 20 | 3468.75 | 28860 | 32328.75 |  |  | 473.5758 | 3419.6325 | 4.843% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1035.5265 | 1014.8214 | 994.5303 | 974.6449 | 955.1571 | 936.0589 | 917.3426 | 899.0006 | 881.0253 | 863.4094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Start/stop inverter (reboot to clear unknown error) | Corrective | Inverter | 1 | 0 | 0 | EPC | inverter | Inspector | 25.1731 | 1 | 3 | Interval | 1 | 0.25 | 0 | 6.2933 | 0 | 6.2933 |  |  | 7.7984 | 79.0841 | 0.112% | 6.4191 | 6.5475 | 6.6785 | 6.812 | 6.9483 | 7.0872 | 7.229 | 7.3736 | 7.521 | 7.6715 | 7.8249 | 7.9814 | 8.141 | 8.3038 | 8.4699 | 8.6393 | 8.8121 | 8.9883 | 9.1681 | 9.3515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter fan motor | Corrective | Inverter | 0 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 15 | 1 | Weibull | 1 | 1 | 120 | 24.0385 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace MC Connectors between modules | Corrective | DC wiring | 1 | 1 | 1 | Module (Product) | modules | PV module/array Specialist | 24.0385 | 25 | 1 | Weibull | 1443 | 0.1 | 5 | 3468.75 | 7215 | 10683.75 |  |  | 156.5036 | 1130.0931 | 1.601% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342.2126 | 335.3702 | 328.6645 | 322.0929 | 315.6528 | 309.3414 | 303.1561 | 297.0946 | 291.1543 | 285.3327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate ground fault | Corrective | DC Wiring | 1 | 1 | 1 | EPC |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 1 | 4 | 0 | 92.7885 | 0 | 92.7885 |  |  | 1.3592 | 9.8149 | 0.0139% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9721 | 2.9127 | 2.8545 | 2.7974 | 2.7414 | 2.6866 | 2.6329 | 2.5803 | 2.5287 | 2.4781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair or replace damage to module frame | Corrective | PV module | 0 | 1 | 1 | Module (Product) | modules | Mechanic | 21.2308 | 50 | 3 | Weibull | 1443 | 0.25 | 50 | 7659 | 72150 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace protective devices (breakers) in building panel | Corrective | AC wiring | 1 | 1 | 1 | N/A |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 3 | 0.25 | 10 | 17.3978 | 30 | 47.3978 |  |  | 1.544 | 17.0835 | 0.0242% | 1.858 | 1.8209 | 1.7844 | 1.7488 | 1.7138 | 1.6795 | 1.646 | 1.613 | 1.5808 | 1.5492 | 1.5182 | 1.4879 | 1.4581 | 1.4289 | 1.4004 | 1.3724 | 1.3449 | 1.318 | 1.2917 | 1.2659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair ground fault | Corrective | DC Wiring | 1 | 1 | 1 | EPC |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 1 | 1 | 20 | 23.1971 | 20 | 43.1971 |  |  | 0.63278 | 4.5693 | 0.006472% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3837 | 1.356 | 1.3289 | 1.3023 | 1.2763 | 1.2507 | 1.2257 | 1.2012 | 1.1772 | 1.1537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter AC fuse(s) | Corrective | AC wiring | 1 | 1 | 1 | EPC |  | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 3 | 0.15 | 10 | 6.4904 | 30 | 36.4904 |  |  | 0.53454 | 3.8598 | 0.005467% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1688 | 1.1455 | 1.1226 | 1.1001 | 1.0781 | 1.0566 | 1.0354 | 1.0147 | 0.99444 | 0.97455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair cracking of PV module back sheet | Corrective | PV module | 0 | 1 | 1 | Module (Product) | modules | Journeyman electrician | 14.4231 | 50 | 3 | Weibull | 1443 | 0.1 | 25 | 2081.25 | 36075 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair or replace rack parts damaged by corrosion or physical damage | Corrective | PV Array | 1 | 1 | 1 | EPC |  | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 1 | 200 | 2187.7139 | 20608.8993 | 22796.6132 |  |  | 554.1912 | 3741.5775 | 5.299% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604.7333 | 715.6598 | 831.3717 | 949.6443 | 1067.9454 | 1183.4954 | 1293.3505 | 1394.5051 | 1484.0112 | 1559.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace fuse(s) on DC source circuits to inverter | Corrective | DC wiring | 1 | 1 | 1 | EPC |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 18 | 0.08 | 5 | 33.4038 | 90 | 123.4038 |  |  | 1.8077 | 13.0533 | 0.01849% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9528 | 3.8737 | 3.7963 | 3.7204 | 3.646 | 3.5731 | 3.5016 | 3.4316 | 3.363 | 3.2958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
manual reset of arc-fault trip (NEC 690.11) | Corrective | Inverter | 1 | 1 | 1 | EPC | inverter | Inverter specialist | 24.0385 | 25 | 1 | Weibull | 1 | 0.08 | 0 | 1.9231 | 0 | 1.9231 |  |  | 0.028171 | 0.20342 | 0.0002881% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061598 | 0.060367 | 0.05916 | 0.057977 | 0.056818 | 0.055682 | 0.054568 | 0.053477 | 0.052408 | 0.05136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seal Leaking Junction Box | Corrective | DC Wiring | 1 | 1 | 1 | Module (Product) | modules | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 1443 | 0.25 | 10 | 5203.125 | 14430 | 19633.125 |  |  | 287.6008 | 2076.7296 | 2.941% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 628.8712 | 616.2971 | 603.9744 | 591.8981 | 580.0632 | 568.465 | 557.0986 | 545.9596 | 535.0432 | 524.3452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate line-to-line fault | Corrective | AC Wiring | 1 | 1 | 1 | EPC |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 1 | 1 | 0 | 23.1971 | 0 | 23.1971 |  |  | 0.33981 | 2.4537 | 0.003475% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74303 | 0.72817 | 0.71361 | 0.69934 | 0.68536 | 0.67166 | 0.65823 | 0.64507 | 0.63217 | 0.61953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate underground AC wiring | Corrective | AC Wiring | 0 | 1 | 1 | N/A |  | Utilities locator | 18.5144 | 25 | 3 | Weibull | 1 | 4 | 0 | 74.0577 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair line-to-line fault | Corrective | AC Wiring | 1 | 1 | 1 | N/A |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 1 | 1 | 20 | 23.1971 | 20 | 43.1971 |  |  | 1.4072 | 15.5694 | 0.02205% | 1.6933 | 1.6595 | 1.6263 | 1.5938 | 1.5619 | 1.5307 | 1.5001 | 1.4701 | 1.4407 | 1.4119 | 1.3837 | 1.356 | 1.3289 | 1.3023 | 1.2763 | 1.2507 | 1.2257 | 1.2012 | 1.1772 | 1.1537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace broken/crushed AC wiring conduit and fittings | Corrective | AC wiring | 0 | 1 | 1 | N/A | strings | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 103.0445 | 0.25 | 10 | 371.5547 | 1030.445 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate underground DC wiring | Corrective | DC wiring | 0 | 1 | 1 | N/A |  | Utilities locator | 18.5144 | 25 | 1 | Weibull | 1 | 2 | 0 | 37.0288 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace broken/crushed DC wiring conduit and fittings | Corrective | DC wiring | 0 | 1 | 1 | N/A |  | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 1 | 4 | 100 | 57.6923 | 100 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace failed DC fuses in combiner box | Corrective | DC wiring | 1 | 1 | 1 | N/A | strings | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 103.0445 | 0.08 | 1 | 118.8975 | 103.0445 | 221.942 |  |  | 7.23 | 79.9939 | 0.1133% | 8.7002 | 8.5262 | 8.3557 | 8.1887 | 8.0249 | 7.8645 | 7.7072 | 7.5531 | 7.4021 | 7.2541 | 7.1091 | 6.9669 | 6.8276 | 6.6911 | 6.5573 | 6.4262 | 6.2977 | 6.1718 | 6.0484 | 5.9274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-route conduit | Corrective | DC wiring | 0 | 1 | 1 | N/A |  | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 1 | 4 | 100 | 57.6923 | 100 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RE-install inverter control software | Corrective | Inverter | 0 | 1 | 1 | EPC | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 0 | 24.0385 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace 24VDC power supply for inverter controls | Corrective | Inverter | 0 | 1 | 1 | EPC | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 120 | 24.0385 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace AC contactor in inverter | Corrective | Inverter | 0 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 2 | 40 | 48.0769 | 40 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace capacitors in inverter | Corrective | Inverter | 0 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 2 | 20000 | 48.0769 | 20000 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace DC contactor in inverter | Corrective | Inverter | 0 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 2 | 40 | 48.0769 | 40 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace fuses internal to inverter | Corrective | Inverter | 0 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 0.25 | 25 | 6.0096 | 25 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace GFI components in inveter | Corrective | Inverter | 0 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 120 | 24.0385 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace IGBT driver card/board; diagnose with fault code | Corrective | Inverter | 0 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 2 | 1000 | 48.0769 | 1000 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace IGBT matrix in inverter | Corrective | Inverter | 0 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 4 | 80000 | 96.1538 | 80000 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inductors (coils) in inverter | Corrective | Inverter | 0 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 4 | 20000 | 96.1538 | 20000 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter control card (PWM signal, voltage, phase, frequency, shut-down); diagnose with fault code | Corrective | Inverter | 0 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 1000 | 24.0385 | 1000 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter data acquisition card/board (also called system input module); diagnose with fault code | Corrective | Inverter | 0 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 1000 | 24.0385 | 1000 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter relay/switch | Corrective | Inverter | 0 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 55 | 24.0385 | 55 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace maximum power point tracker card/board; diagnose with fault code | Corrective | Inverter | 0 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 1000 | 24.0385 | 1000 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace overvoltage surge suppressors for inverter | Corrective | Inverter | 0 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 25 | 24.0385 | 25 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace terminal block | Corrective | Inverter | 0 | 1 | 1 | Inverter | Combiner Box | Journeyman electrician | 14.4231 | 5 | 3 | Interval | 18 | 0.25 | 10 | 64.9038 | 180 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Restore lost internet connection | Corrective | Monitoring | 1 | 1 | 1 | N/A | Site | Network/IT | 33.25 | 20 | 3 | Interval | 1 | 1 | 0 | 33.25 | 0 | 33.25 |  |  | 2.4704 | 12.7679 | 0.01808% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Excavate and replace failed foundation element | Corrective | PV Array | 0 | 1 | 1 | N/A |  | Structural engineer | 40.4519 | 25 | 3 | Weibull | 103.0445 | 4 | 400 | 16673.3922 | 41217.7986 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair roof leaks | Corrective | Roof | 0 | 1 | 1 | N/A | acres | Roofing | 16.4519 | 25 | 1 | Weibull | 2.3153 | 8 | 400 | 304.7263 | 926.1115 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-roof (new roof) | Corrective | Roof | 0 | 1 | 1 | N/A | acres | Roofing | 16.4519 | 30 | 4 | Weibull | 2.3153 | 24 | 75000 | 914.1789 | 173645.9016 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace transformer | Corrective | Transformer | 0 | 0 | 0 | N/A | Transformer | Master electrician | 23.1971 | 50 | 2 | Weibull | 1 | 4 | 22000 | 92.7885 | 22000 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-tap transformer | Corrective | Transformer | 0 | 0 | 0 | N/A | Transformer | Master electrician | 23.1971 | 25 | 3 | Weibull | 1 | 2 | 0 | 46.3942 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meet with key site staff to continue awareness, question any issues, and report on findings. | Administration | Documents | 1 | 0 | 0 | N/A |  | Administrator | 16.6635 | 1 | 1 | interval | 1 | 2 | 0 | 33.3269 | 0 | 33.3269 |  |  | 41.2976 | 418.8015 | 0.5932% | 33.9935 | 34.6733 | 35.3668 | 36.0741 | 36.7956 | 37.5315 | 38.2822 | 39.0478 | 39.8288 | 40.6253 | 41.4378 | 42.2666 | 43.1119 | 43.9742 | 44.8537 | 45.7507 | 46.6657 | 47.5991 | 48.551 | 49.5221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bird Cleaning | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | acres | Cleaner | 10.6779 | 0.5 | 1 | interval | 1 | 4 | 120 | 42.7115 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Snow Removal | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | acres | Mower/Trimmer | 21.2308 | 0.5 | 1 | interval | 1 | 2 | 100 | 42.4615 | 100 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pollen Cleaning | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | acres | Cleaner | 10.6779 | 1 | 1 | interval | 1 | 4 | 120 | 42.7115 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dust Removal | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | acres | Cleaner | 10.6779 | 1 | 1 | interval | 1 | 4 | 120 | 42.7115 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Daily Operations and Performance Monitoring | Preventive | Asset Management | 0 | 0 | 0 | N/A |  | Administrator | 16.6635 | 0.083333 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monitor alarms and site-specific altert parameters | Preventive | Asset Management | 0 | 0 | 0 | N/A |  | Administrator | 16.6635 | 0.083333 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Calibrate or replace weather sensors & meters | Preventive | Electrical | 0 | 0 | 0 | N/A | Weather Station | Network/IT | 33.25 | 5 | 1 | interval | 1 | 0.5 | 500 | 16.625 | 500 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check Electrical connections & enclosure for tracking motor/controller | Preventive | Tracker | 0 | 0 | 0 | N/A | Controller | Inspector | 25.1731 | 1 | 1 | interval | 1 | 0.083333 | 0 | 2.0978 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check Grounding Braids for wear | Preventive | Tracker | 0 | 0 | 0 | N/A | Structure | Inspector | 25.1731 | 1 | 1 | interval | 206.089 | 0.004 | 0 | 20.7516 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Anemometer inspection | Preventive | Tracker | 0 | 0 | 0 | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 1 | 0.1 | 0 | 2.5173 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Driveshaft torque check & visual inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | Driveshaft | Inspector | 25.1731 | 1 | 1 | interval | 0 | 0.0083333 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gearbox lubrication | Preventive | Tracker | 0 | 0 | 0 | N/A | block | Mechanic | 21.2308 | 0.5 | 1 | interval | 103.0445 | 0.25 | 0 | 546.9285 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inclinometer inspection | Preventive | Tracker | 0 | 0 | 0 | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 1 | 0.1 | 0 | 2.5173 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Limit switch inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | block | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical labor mobilization | Preventive | Mechanical | 0 | 0 | 0 | EPC | Site | Mechanic | 21.2308 | 1 | 1 | interval | 1 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Module table inpsection | Preventive | Tracker | 0 | 0 | 0 | N/A | connection | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Screw jack greasing | Preventive | Tracker | 0 | 0 | 0 | N/A | block | Mechanic | 21.2308 | 0.5 | 1 | interval | 103.0445 | 0.25 | 0 | 546.9285 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Screw jack inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | block | Inspector | 25.1731 | 0.5 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slew gear lubrication | Preventive | Tracker | 0 | 0 | 0 | N/A | Slew Gear | Mechanic | 21.2308 | 3 | 1 | interval | 0 | 0.25 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slew gear torque check & wear inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | Slew Gear | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.016667 | 0 | 43.2325 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Torque inspection | Preventive | Mechanical | 0 | 0 | 0 | N/A | block | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tracking Controller inspection | Preventive | Tracker | 0 | 0 | 0 | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Universal joint greasing (zirc fitting) | Preventive | Tracker | 0 | 0 | 0 | N/A | Driveshaft | Mechanic | 21.2308 | 0.5 | 1 | interval | 0 | 0.16667 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Universal joint inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | Driveshaft | Inspector | 25.1731 | 1 | 1 | interval | 0 | 0.0083333 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Spot-check monitoring instruments (pyranometer, etc) with hand-held instruments to ensure that they are operational and within specifications. | Preventive | Monitoring | 0 | 0 | 0 | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 1 | 1 | 0 | 25.1731 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect ballasted, non-penetrating mounting system for abnormal movement | Preventive | PV Array | 0 | 0 | 0 | N/A | rows | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.08 | 0 | 207.5158 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remove bird nests from array and rack area. | Preventive | PV Array | 0 | 0 | 0 | N/A | Acres | Pest control | 14.5865 | 1 | 1 | interval | 2.3153 | 4 | 0 | 135.0876 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walk through each row of the PV array and check the PV modules for any damage. Report any damage to rack and damaged modules for warranty replacement. Note location and serial number of questionable modules. | Preventive | PV Array | 0 | 0 | 0 | N/A | Acres | Inspector | 25.1731 | 1 | 1 | interval | 2.3153 | 0.5 | 0 | 29.1413 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lubricate tracker mounting bearings/gimbals | Preventive | Tracker | 0 | 0 | 0 | N/A |  | Mechanic | 21.2308 | 1 | 1 | interval | 103.0445 | 0.15 | 1 | 328.1571 | 103.0445 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect transformer meter, oil and tempertaure gauges | Preventive | Transformer | 0 | 0 | 0 | N/A |  | Master electrician | 23.1971 | 1 | 1 | interval | 1 | 0.25 | 0 | 5.7993 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracking controller power supply fan filter | Corrective | Tracker | 0 | 1 | 1 | EPC | Controller | Mechanic | 21.2308 | 2 | 1 | interval | 103.0445 | 0.16667 | 25 | 364.619 | 2576.1124 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair/replace tracker drive shaft | Corrective | Tracker | 0 | 1 | 1 | N/A | row | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 0.5 | 120 | 1093.857 | 12365.3396 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace hydraulic cylinder | Corrective | Tracker | 0 | 1 | 1 | N/A |  | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 0.5 | 120 | 1093.857 | 12365.3396 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracker drive bearing | Corrective | Tracker | 0 | 1 | 1 | N/A | row | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 0.5 | 40 | 1093.857 | 4121.7799 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracker motor controller | Corrective | Tracker | 0 | 1 | 1 | N/A |  | Journeyman electrician | 14.4231 | 25 | 3 | Weibull | 103.0445 | 0.5 | 250 | 743.1093 | 25761.1241 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracker mount bearing | Corrective | Tracker | 0 | 1 | 1 | N/A |  | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 0.5 | 40 | 1093.857 | 4121.7799 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace/upgrade tracker control software | Corrective | Tracker | 0 | 1 | 1 | N/A |  | Network/IT | 33.25 | 25 | 3 | Weibull | 103.0445 | 1 | 0 | 3426.2295 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manage inventory of spare parts | Administration | Asset Management | 0 | 1 | 1 | Monitoring |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Confirm availability and take any measures to secure operating instructions, warranties and performance guarantees, and other project documentation. | Administration | Documents | 0 | 0 | 0 | N/A |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Document all O&M activities in a workbook available to all service personnel. | Administration | Documents | 0 | 0 | 0 | N/A |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Review O&M agreements and ensure that services are actually provided | Administration | Documents | 0 | 0 | 0 | N/A |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Update record with preventative maintenance activities and track any problems or warranty issues and secure the record on-site. | Administration | Documents | 0 | 0 | 0 | N/A |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maintain a log of cumulative power delivery (kWh to date) and chart this value against date. Chart the value even for uneven or infrequent intervals. Explain variation by season or weather. | Administration | Meter | 0 | 0 | 0 | N/A |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 0.5 | 0 | 8.3317 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 8640.0808 | 70603.9923 | 100% | 2497.7197 | 2573.3741 | 2597.6475 | 2676.378 | 3249.6955 | 2863.1599 | 2891.0642 | 2977.9457 | 3006.995 | 3702.489 | 12775.7607 | 13093.4262 | 13319.082 | 13696.0316 | 14634.7541 | 14384.0071 | 14679.943 | 15117.7997 | 15419.0657 | 16645.2769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Residential Rooftop Details
Residential System (< 10kWp)
Warning: You have selected Grount-Mount Fixed Tilt (> 100kW) on the Inputs and Summary page. Please go back and select 'Residential' System Type on Inputs & Summary Page
Inputs |  |  | Lifetime NPV by Service Type |  |  |  |  | Lifetime NPV by Component Type
Analysis Period (Project Life) | 20 |  | Service | Avg. Cost/Yr | NPV (Life) | % of Total |  | Component | Avg. Cost/Yr | NPV (Life) | % of Total
Discount Rate | 7% |  | Administrator | 68.8092 | 581.2229 | 1.702% |  | Documents | 0 | 0 | 0%
Inflation Rate | 2% |  | Cleaner | 0 | 0 | 0% |  | Asset Management | 48.688 | 411.2613 | 1.204%
Truck Rental Cost/ day | 100 |  | Inverter specialist | 1189.3299 | 8869.3238 | 25.97% |  | PV Array | 20.1212 | 169.9616 | 0.4976%
Working Hours/year | 2080 |  | Inspector | 35.4776 | 346.5934 | 1.015% |  | Cleaning/Veg | 0 | 0 | 0%
System Size (Wp DC) | 440000 |  | Journeyman electrician | 2873.4741 | 19668.491 | 57.58% |  | Electrical | 46.9846 | 427.8642 | 1.253%
Energy Yield (kWh/kWp/year) | 1596 |  | PV module/array Specialist | 630.0794 | 4549.7256 | 13.32% |  | Meter | 0 | 0 | 0%
Module Power (W STC) | 305 |  | Network/IT | 0 | 0 | 0% |  | PV Module | 2873.4741 | 19668.491 | 57.58%
Number of Modules | 1443 |  | Master electrician | 19.327 | 142.9954 | 0.4186% |  | DC Wiring | 632.0715 | 4564.1097 | 13.36%
Module Type/ Degradation | Mulit-crystal Silicon:0.64%/year |  | Mechanic | 0 | 0 | 0% |  | Mechanical | 0 | 0 | 0%
Module Encapsulant | Ethyl Vinyl Acetate (EVA) |  | Designer | 0 | 0 | 0% |  | AC Wiring | 1.544 | 17.0835 | 0.05001%
Modules per String | 14 |  | Pest control | 0 | 0 | 0% |  | Inverter | 1193.6139 | 8899.5807 | 26.05%
Number of Strings | 103.0445 |  | Roofing | 0 | 0 | 0% |  | Monitoring | 0 | 0 | 0%
Strings per Combiner Box | 6 |  | Structural engineer | 0 | 0 | 0% |  | Total | 4816.4973 | 34158.352 | 100%
Number of Combiner Boxes | 18 |  | Mower/Trimmer | 0 | 0 | 0%
Combiner boxes per DC disconnect | 1 |  | Utilities locator | 0 | 0 | 0%
Number of DC Disconnects | 18 |  | Total | 4816.4973 | 34158.352 | 100%
Inverter Type | String Inverter
Inverter Warranty (years) | 10
Number of Inverters | 1
Inverter Capacity (kWp) | 400 | [7 empty] | `
Number of Transformers | 1
Detailed Measures | [23 empty] | Annual Cash Flow
Activity Description | Activity Type | Component Type | Applicable ? (1= yes, 0 = no) | Covered by Warranty - Materials (1=yes, 0=no) | Covered by Warranty - Labor (1=yes, 0=no) | Warranty or Service Package Type | Applicable Unit | Service Category | Labor Rate per Hour | Mean Interval (years) | Weibull or Lognormal Shape Factor | Type of Distribution | Approx. Number of Units | Labor hrs per unit | Material/ Other Cost per unit | Total Labor Cost | Total Matl and Other Cost | Total Cost for Measure | Notes | Reference | Average Annual Expense | NPV (Project Life) | % of Total NPV | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
Monitoring annual service package | Preventive | Asset Management | 1 | 1 | 1 | Monitoring | System | Administrator | 0 | 1 | 1 | interval | 1 | 0 | 50 | 0 | 50 | 50 |  |  | 48.688 | 411.2613 | 1.204% | 0 | 0 | 0 | 0 | 0 | 56.3081 | 57.4343 | 58.583 | 59.7546 | 60.9497 | 62.1687 | 63.4121 | 64.6803 | 65.9739 | 67.2934 | 68.6393 | 70.0121 | 71.4123 | 72.8406 | 74.2974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter inspection | Preventive | Electrical | 1 | 1 | 1 | N/A | Inverter | Inspector | 25.1731 | 1 | 1 | interval | 1 | 1 | 0 | 25.1731 | 0 | 25.1731 |  |  | 31.1936 | 316.3365 | 0.9261% | 25.6765 | 26.1901 | 26.7139 | 27.2481 | 27.7931 | 28.349 | 28.916 | 29.4943 | 30.0842 | 30.6858 | 31.2996 | 31.9255 | 32.5641 | 33.2153 | 33.8796 | 34.5572 | 35.2484 | 35.9534 | 36.6724 | 37.4059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrical labor mobilization | Preventive | Electrical | 1 | 1 | 1 | EPC | Site | Master electrician | 23.1971 | 1 | 1 | interval | 1 | 1 | 0 | 23.1971 | 0 | 23.1971 |  |  | 15.791 | 111.5278 | 0.3265% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.8427 | 29.4196 | 30.0079 | 30.6081 | 31.2203 | 31.8447 | 32.4816 | 33.1312 | 33.7938 | 34.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check position of disconnect switches and breakers. | Preventive | AC Wiring | 0 | 0 | 0 | N/A | Disconnect Box | Inspector | 25.1731 | 1 | 1 | interval | 18 | 0.08 | 0 | 36.2492 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect electrical boxes for corrosion or intrusion of water or insects. Seal boxes if required. | Preventive | AC Wiring | 0 | 0 | 0 | N/A | Combiner Box | Inspector | 25.1731 | 1 | 1 | interval | 18 | 0.08 | 0 | 36.2492 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check proper position of DC disconnect switches. | Preventive | DC Wiring | 0 | 0 | 0 | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 18 | 0.08 | 0 | 36.2492 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DC circuit test & combiner box inspection | Preventive | Electrical | 0 | 0 | 0 | N/A | Combiner Box | PV module/array Specialist | 24.0385 | 1 | 1 | interval | 18 | 0.083333 | 0 | 36.0577 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV module torque check & visual inspection | Preventive | Mechanical | 0 | 0 | 0 | N/A | Rail/ Fastener | PV module/array Specialist | 24.0385 | 5 | 1 | interval | 1648.7119 | 0.0083333 | 0 | 330.2708 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV module electrical connection check | Preventive | Electrical | 0 | 0 | 0 | N/A | PV Module | PV module/array Specialist | 24.0385 | 5 | 1 | Interval | 1442.623 | 0.0041667 | 0 | 144.4935 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Racking torque check & inspection | Preventive | Mechanical | 0 | 0 | 0 | N/A | Structure | Inspector | 25.1731 | 5 | 1 | interval | 103.0445 | 0.0083333 | 0 | 21.6162 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check grounding hardware | Preventive | Electrical | 0 | 0 | 0 | N/A | Structure | Master electrician | 23.1971 | 1 | 1 | interval | 1 | 0.00055556 | 0 | 0.012887 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical labor mobilization | Preventive | Mechanical | 0 | 1 | 1 | EPC | Site | Mechanic | 21.2308 | 1 | 1 | interval | 1 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter | Corrective | Inverter | 1 | 1 | 1 | Inverter | Inverter | Inverter specialist | 24.0385 | 10 | 1 | Weibull | 1 | 0 | 80300 | 0 | 80300 | 80300 | $300 flat fee |  | 1189.3017 | 8869.1204 | 25.96% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3323.4833 | 3067.3563 | 2830.9679 | 2612.797 | 2411.4397 | 2225.6001 | 2054.0823 | 1895.7828 | 1749.6827 | 1614.8419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace modules failing performance test or IR scan | Corrective | PV module | 1 | 1 | 1 | Module (Product) | modules | Journeyman electrician | 14.4231 | 50 | 2 | Weibull | 1443 | 0.15 | 244 | 3121.875 | 352092 | 355213.875 |  |  | 2721.5633 | 18665.2308 | 54.64% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3703.0078 | 4082.7036 | 4466.4984 | 4853.5741 | 5243.0891 | 5634.1822 | 6025.9748 | 6417.5748 | 6808.08 | 7196.5811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dispatch contractor in response to alarms, alerts, or contact by others | Corrective | PV Array | 1 | 1 | 1 | Monitoring |  | Administrator | 16.6635 | 1 | 1 | Interval | 1 | 1 | 4 | 16.6635 | 4 | 20.6635 |  |  | 20.1212 | 169.9616 | 0.4976% | 0 | 0 | 0 | 0 | 0 | 23.2704 | 23.7358 | 24.2105 | 24.6947 | 25.1886 | 25.6924 | 26.2063 | 26.7304 | 27.265 | 27.8103 | 28.3665 | 28.9338 | 29.5125 | 30.1028 | 30.7048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace MC connector lead to combiner box | Corrective | DC wiring | 1 | 1 | 1 | Module (Product) | modules | PV module/array Specialist | 24.0385 | 25 | 1 | Weibull | 1443 | 0.1 | 20 | 3468.75 | 28860 | 32328.75 |  |  | 473.5758 | 3419.6325 | 10.01% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1035.5265 | 1014.8214 | 994.5303 | 974.6449 | 955.1571 | 936.0589 | 917.3426 | 899.0006 | 881.0253 | 863.4094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Start/stop inverter (reboot to clear unknown error) | Corrective | Inverter | 1 | 1 | 1 | EPC | inverter | Inspector | 25.1731 | 1 | 3 | Interval | 1 | 0.25 | 0 | 6.2933 | 0 | 6.2933 |  |  | 4.284 | 30.257 | 0.08858% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8249 | 7.9814 | 8.141 | 8.3038 | 8.4699 | 8.6393 | 8.8121 | 8.9883 | 9.1681 | 9.3515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter fan motor | Corrective | Inverter | 0 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 15 | 1 | Weibull | 1 | 1 | 120 | 24.0385 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace MC Connectors between modules | Corrective | DC wiring | 1 | 1 | 1 | Module (Product) | modules | PV module/array Specialist | 24.0385 | 25 | 1 | Weibull | 1443 | 0.1 | 5 | 3468.75 | 7215 | 10683.75 |  |  | 156.5036 | 1130.0931 | 3.308% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342.2126 | 335.3702 | 328.6645 | 322.0929 | 315.6528 | 309.3414 | 303.1561 | 297.0946 | 291.1543 | 285.3327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate ground fault | Corrective | DC Wiring | 1 | 1 | 1 | EPC |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 1 | 4 | 0 | 92.7885 | 0 | 92.7885 |  |  | 1.3592 | 9.8149 | 0.02873% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9721 | 2.9127 | 2.8545 | 2.7974 | 2.7414 | 2.6866 | 2.6329 | 2.5803 | 2.5287 | 2.4781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair or replace damage to module frame | Corrective | PV module | 0 | 1 | 1 | Module (Product) | modules | Mechanic | 21.2308 | 50 | 3 | Weibull | 1443 | 0.25 | 50 | 7659 | 72150 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace protective devices (breakers) in building panel | Corrective | AC wiring | 1 | 1 | 1 | N/A |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 3 | 0.25 | 10 | 17.3978 | 30 | 47.3978 |  |  | 1.544 | 17.0835 | 0.05001% | 1.858 | 1.8209 | 1.7844 | 1.7488 | 1.7138 | 1.6795 | 1.646 | 1.613 | 1.5808 | 1.5492 | 1.5182 | 1.4879 | 1.4581 | 1.4289 | 1.4004 | 1.3724 | 1.3449 | 1.318 | 1.2917 | 1.2659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair ground fault | Corrective | DC Wiring | 1 | 1 | 1 | EPC |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 1 | 1 | 20 | 23.1971 | 20 | 43.1971 |  |  | 0.63278 | 4.5693 | 0.01338% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3837 | 1.356 | 1.3289 | 1.3023 | 1.2763 | 1.2507 | 1.2257 | 1.2012 | 1.1772 | 1.1537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter AC fuse(s) | Corrective | AC wiring | 0 | 1 | 1 | EPC |  | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 3 | 0.15 | 10 | 6.4904 | 30 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair cracking of PV module back sheet | Corrective | PV module | 1 | 1 | 1 | Module (Product) | modules | Journeyman electrician | 14.4231 | 50 | 3 | Weibull | 1443 | 0.1 | 25 | 2081.25 | 36075 | 38156.25 |  |  | 151.9108 | 1003.2602 | 2.937% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136.3138 | 164.9445 | 196.7128 | 231.6871 | 269.9206 | 311.4502 | 356.2937 | 404.4479 | 455.8866 | 510.5585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair or replace rack parts damaged by corrosion or physical damage | Corrective | PV Array | 0 | 1 | 1 | EPC |  | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 1 | 200 | 2187.7139 | 20608.8993 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace fuse(s) on DC source circuits to inverter | Corrective | DC wiring | 0 | 1 | 1 | EPC |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 18 | 0.08 | 5 | 33.4038 | 90 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
manual reset of arc-fault trip (NEC 690.11) | Corrective | Inverter | 1 | 1 | 1 | EPC | inverter | Inverter specialist | 24.0385 | 25 | 1 | Weibull | 1 | 0.08 | 0 | 1.9231 | 0 | 1.9231 |  |  | 0.028171 | 0.20342 | 0.0005955% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061598 | 0.060367 | 0.05916 | 0.057977 | 0.056818 | 0.055682 | 0.054568 | 0.053477 | 0.052408 | 0.05136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bird Cleaning | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | acres | Cleaner | 10.6779 | 0.5 | 1 | interval | 1 | 4 | 120 | 42.7115 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Snow Removal | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | acres | Mower/Trimmer | 21.2308 | 0.5 | 1 | interval | 1 | 2 | 100 | 42.4615 | 100 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pollen Cleaning | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | acres | Cleaner | 10.6779 | 1 | 1 | interval | 1 | 4 | 120 | 42.7115 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dust Removal | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | acres | Cleaner | 10.6779 | 1 | 1 | interval | 1 | 4 | 120 | 42.7115 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Daily Operations and Performance Monitoring | Preventive | Asset Management | 0 |  |  | N/A |  | Administrator | 16.6635 | 0.083333 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monitor alarms and site-specific altert parameters | Preventive | Asset Management | 0 |  |  | N/A |  | Administrator | 16.6635 | 0.083333 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor available by email and phone 24x7x365 | Preventive | PV Array | 0 |  |  | N/A |  | Administrator | 16.6635 | 1 | 1 | interval | 1 | 12 | 0 | 199.9615 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Install software updates, inverter and other | Preventive | Electrical | 0 |  |  | N/A | NCU | Inverter specialist | 24.0385 | 5 | 1 | interval | 1 | 1 | 500 | 24.0385 | 500 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check central SCADA/network manager | Preventive | Electrical | 0 |  |  | N/A | NCU | Network/IT | 33.25 | 1 | 1 | interval | 1 | 0.25 | 0 | 8.3125 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Corrosion inpsection | Preventive | Mechanical | 0 |  |  | N/A | connection | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Galvanazation inspection | Preventive | Mechanical | 0 |  |  | N/A | connection | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Use infrared camera to inspect for hot spots; bypass diode failure | Preventive | PV Module | 0 |  |  | N/A | strings | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.15 | 0 | 389.0921 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-torque all electrical connections on AC side of system. | Preventive | AC Wiring | 0 |  |  | N/A |  | Journeyman electrician | 14.4231 | 1 | 1 | interval | 1 | 0.5 | 0 | 7.2115 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test open circuit voltage or IV curve of series strings of modules | Preventive | PV Array | 0 |  |  | N/A | strings | PV module/array Specialist | 24.0385 | 1 | 1 | interval | 103.0445 | 0.15 | 0 | 371.5547 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AC disconnect box inspection | Preventive | Electrical | 0 |  |  | N/A | Disconnect Box | Inspector | 25.1731 | 1 | 1 | interval | 1 | 0.25 | 0 | 6.2933 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect cabling for signs of cracks, defects, pulling out of connections; overheating, arcing, short or open circuits, ground faults in wiring and condition of wire insulation and protective materials.. | Preventive | DC Wiring | 0 |  |  | N/A | strings | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test modules showing corrosion of ribbons to junction box | Preventive | PV Module | 0 |  |  | N/A | modules | Journeyman electrician | 14.4231 | 5 | 1 | interval | 1443 | 0.08 | 0 | 1665 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test output of modules that exhibit cracked glass, bubble formation oxidation of busbars, discoloration of busbars, or PV module hot spots (bypass diode failure) | Preventive | PV Module | 0 |  |  | N/A | modules | Journeyman electrician | 14.4231 | 5 | 1 | interval | 1443 | 0.08 | 0 | 1665 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exercise operation of all protection devices. | Preventive | AC Wiring | 0 |  |  | N/A |  | Journeyman electrician | 14.4231 | 1 | 1 | interval | 2 | 0.08 | 0 | 2.3077 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Array cleaning | Preventive | Cleaning/Veg | 0 |  |  | N/A | Acre | Cleaner | 10.6779 | 0.25 | 1 | interval | 1 | 4 | 120 | 42.7115 | 120 | 0 | 2 gal fuel/acre @$4/gal + 500 gal H2O/acre @$0.40/gal |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
General Cleaning/Veg Mobilization | Preventive | Cleaning/Veg | 0 |  |  | N/A | Site | Mower/Trimmer | 21.2308 | 1 | 1 | interval | 1 | 4 | 120 | 84.9231 | 120 | 0 | Other cost = water truckr rental |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation management (mowing, trimming) per acre | Preventive | Cleaning/Veg | 0 |  |  | N/A | Acre | Mower/Trimmer | 21.2308 | 0.25 | 1 | interval | 2.3153 | 2 | 0 | 98.3103 | 0 | 0 | Other cost = 1 gal fuel/acre @ $4/gal + $10/acre mowing consumables |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Look for any signs of intrusion by pests such as insects and rodents. Remove any nests from electrical boxes (junction boxes, pull boxes, combiner boxes) or around the array. Use safe sanitation practices because pests may carry disease. | Preventive | DC Wiring | 0 |  |  | N/A |  | Pest control | 14.5865 | 1 | 1 | interval | 37 | 0.15 | 1 | 80.9553 | 37 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Open each combiner box and check that no fuses have blown and that all electrical connections are tight. Use an infrared camera for identifying loose connections because they are warmer than good connections when passing current. | Preventive | DC Wiring | 0 |  |  | N/A | Combiner Box | Journeyman electrician | 14.4231 | 1 | 1 | interval | 18 | 0.15 | 0 | 38.9423 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-torque all electrical connections in combiner box. | Preventive | DC Wiring | 0 |  |  | N/A | Combiner Box | Journeyman electrician | 14.4231 | 1 | 1 | interval | 18 | 0.25 | 0 | 64.9038 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test system grounding with "megger" | Preventive | DC Wiring | 0 |  |  | N/A | strings | Master electrician | 23.1971 | 5 | 1 | interval | 103.0445 | 0.25 | 0 | 597.5838 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Calibrate or replace weather sensors & meters | Preventive | Electrical | 0 |  |  | N/A | Weather Station | Network/IT | 33.25 | 5 | 1 | interval | 1 | 0.5 | 500 | 16.625 | 500 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check Electrical connections & enclosure for tracking motor/controller | Preventive | Tracker | 0 |  |  | N/A | Controller | Inspector | 25.1731 | 1 | 1 | interval | 1 | 0.083333 | 0 | 2.0978 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check Electrical connections (motor) | Preventive | Electrical | 0 |  |  | N/A | Motor | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.083333 | 0 | 216.1623 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check Grounding Braids for wear | Preventive | Electrical | 0 |  |  | N/A | Structure | Inspector | 25.1731 | 1 | 1 | interval | 206.089 | 0.004 | 0 | 20.7516 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transformer/switchgear inspection | Preventive | Electrical | 0 |  |  | N/A | Transformer | Inspector | 25.1731 | 1 | 1 | interval | 1 | 2 | 0 | 50.3462 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Clean (vacuum) dust from heat rejection fins | Preventive | Inverter | 0 | 0 | 0 | N/A | inverter | Cleaner | 10.6779 | 1 | 1 | interval | 1 | 0.1 | 0 | 1.0678 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Performance test: measure incident light while observing temp and energy output. Calculate PV module efficiency as a function of temp and calculate BOS efficiency. Compare readings with diagnostic benchmark (original efficiency of system). | Preventive | Inverter | 0 | 0 | 0 | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 1 | 1 | 0 | 25.1731 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace any air filters on air-cooled equipment such as inverter. | Preventive | Inverter | 0 | 0 | 0 | N/A | inverter | Inverter specialist | 24.0385 | 1 | 1 | interval | 1 | 0.25 | 25 | 6.0096 | 25 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace transient voltage surge suppression devices | Preventive | Inverter | 0 | 1 | 1 | Inverter |  | Master electrician | 23.1971 | 5 | 1 | interval | 1 | 0.5 | 105 | 11.5986 | 105 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test overvoltage surge suppressors in inverter | Preventive | Inverter | 0 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 5 | 1 | interval | 1 | 0.1 | 0 | 2.4038 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Anemometer inspection | Preventive | Tracker | 0 |  |  | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 1 | 0.1 | 0 | 2.5173 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Driveshaft torque check & visual inspection | Preventive | Tracker | 0 |  |  | N/A | Driveshaft | Inspector | 25.1731 | 1 | 1 | interval | 0 | 0.0083333 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gearbox lubrication | Preventive | Tracker | 0 |  |  | N/A | block | Mechanic | 21.2308 | 0.5 | 1 | interval | 103.0445 | 0.25 | 0 | 546.9285 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inclinometer inspection | Preventive | Tracker | 0 |  |  | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 1 | 0.1 | 0 | 2.5173 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Limit switch inspection | Preventive | Tracker | 0 |  |  | N/A | block | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Module table inpsection | Preventive | Tracker | 0 |  |  | N/A | connection | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Screw jack greasing | Preventive | Tracker | 0 |  |  | N/A | block | Mechanic | 21.2308 | 0.5 | 1 | interval | 103.0445 | 0.25 | 0 | 546.9285 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Screw jack inspection | Preventive | Tracker | 0 |  |  | N/A | block | Inspector | 25.1731 | 0.5 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slew gear lubrication | Preventive | Tracker | 0 |  |  | N/A | Slew Gear | Mechanic | 21.2308 | 3 | 1 | interval | 0 | 0.25 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slew gear torque check & wear inspection | Preventive | Tracker | 0 |  |  | N/A | Slew Gear | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.016667 | 0 | 43.2325 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Torque inspection | Preventive | Mechanical | 0 |  |  | N/A | block | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tracking Controller inspection | Preventive | Tracker | 0 |  |  | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Universal joint greasing (zirc fitting) | Preventive | Tracker | 0 |  |  | N/A | Driveshaft | Mechanic | 21.2308 | 0.5 | 1 | interval | 0 | 0.16667 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Universal joint inspection | Preventive | Tracker | 0 |  |  | N/A | Driveshaft | Inspector | 25.1731 | 1 | 1 | interval | 0 | 0.0083333 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Spot-check monitoring instruments (pyranometer, etc) with hand-held instruments to ensure that they are operational and within specifications. | Preventive | Monitoring | 0 |  |  | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 1 | 1 | 0 | 25.1731 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect ballasted, non-penetrating mounting system for abnormal movement | Preventive | PV Array | 0 |  |  | N/A | rows | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.08 | 0 | 207.5158 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remove bird nests from array and rack area. | Preventive | PV Array | 0 |  |  | N/A | Acres | Pest control | 14.5865 | 1 | 1 | interval | 2.3153 | 4 | 0 | 135.0876 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walk through each row of the PV array and check the PV modules for any damage. Report any damage to rack and damaged modules for warranty replacement. Note location and serial number of questionable modules. | Preventive | PV Array | 0 |  |  | N/A | Acres | Inspector | 25.1731 | 1 | 1 | interval | 2.3153 | 0.5 | 0 | 29.1413 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lubricate tracker mounting bearings/gimbals | Preventive | Tracker | 0 |  |  | N/A |  | Mechanic | 21.2308 | 1 | 1 | interval | 103.0445 | 0.15 | 1 | 328.1571 | 103.0445 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect transformer meter, oil and tempertaure gauges | Preventive | Transformer | 0 |  |  | N/A |  | Master electrician | 23.1971 | 1 | 1 | interval | 1 | 0.25 | 0 | 5.7993 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seal Leaking Junction Box | Corrective | DC Wiring | 0 |  |  | Module (Product) | modules | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 1443 | 0.25 | 10 | 5203.125 | 14430 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate line-to-line fault | Corrective | AC Wiring | 0 |  |  | EPC |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 1 | 1 | 0 | 23.1971 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate underground AC wiring | Corrective | AC wiring | 0 |  |  | N/A |  | Utilities locator | 18.5144 | 25 | 3 | Weibull | 1 | 4 | 0 | 74.0577 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair line-to-line fault | Corrective | AC Wiring | 0 |  |  | N/A |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 1 | 1 | 20 | 23.1971 | 20 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace broken/crushed AC wiring conduit and fittings | Corrective | AC wiring | 0 |  |  | N/A | strings | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 103.0445 | 0.25 | 10 | 371.5547 | 1030.445 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate underground DC wiring | Corrective | DC wiring | 0 |  |  | N/A |  | Utilities locator | 18.5144 | 25 | 1 | Weibull | 1 | 2 | 0 | 37.0288 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace broken/crushed DC wiring conduit and fittings | Corrective | DC wiring | 0 |  |  | N/A |  | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 1 | 4 | 100 | 57.6923 | 100 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace failed DC fuses in combiner box | Corrective | DC wiring | 0 |  |  | N/A | strings | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 103.0445 | 0.08 | 1 | 118.8975 | 103.0445 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-route conduit | Corrective | DC wiring | 0 |  |  | N/A |  | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 1 | 4 | 100 | 57.6923 | 100 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracking controller power supply fan filter | Corrective | Electrical | 0 |  |  | N/A | Controller | Mechanic | 21.2308 | 2 | 1 | interval | 1 | 0.16667 | 25 | 3.5385 | 25 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RE-install inverter control software | Corrective | Inverter | 0 | 0 | 0 | EPC | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 0 | 24.0385 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace 24VDC power supply for inverter controls | Corrective | Inverter | 0 | 1 | 0 | EPC | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 120 | 24.0385 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace AC contactor in inverter | Corrective | Inverter | 0 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 2 | 40 | 48.0769 | 40 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace capacitors in inverter | Corrective | Inverter | 0 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 2 | 20000 | 48.0769 | 20000 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace DC contactor in inverter | Corrective | Inverter | 0 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 2 | 40 | 48.0769 | 40 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace fuses internal to inverter | Corrective | Inverter | 0 | 0 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 0.25 | 25 | 6.0096 | 25 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace GFI components in inveter | Corrective | Inverter | 0 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 120 | 24.0385 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace IGBT driver card/board; diagnose with fault code | Corrective | Inverter | 0 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 2 | 1000 | 48.0769 | 1000 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace IGBT matrix in inverter | Corrective | Inverter | 0 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 4 | 80000 | 96.1538 | 80000 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inductors (coils) in inverter | Corrective | Inverter | 0 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 4 | 20000 | 96.1538 | 20000 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter control card (PWM signal, voltage, phase, frequency, shut-down); diagnose with fault code | Corrective | Inverter | 0 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 1000 | 24.0385 | 1000 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter data acquisition card/board (also called system input module); diagnose with fault code | Corrective | Inverter | 0 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 1000 | 24.0385 | 1000 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter relay/switch | Corrective | Inverter | 0 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 55 | 24.0385 | 55 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace maximum power point tracker card/board; diagnose with fault code | Corrective | Inverter | 0 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 1000 | 24.0385 | 1000 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace overvoltage surge suppressors for inverter | Corrective | Inverter | 0 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 25 | 24.0385 | 25 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace terminal block | Corrective | Inverter | 0 | 1 |  | Inverter | Combiner Box | Journeyman electrician | 14.4231 | 5 | 3 | Interval | 18 | 0.25 | 10 | 64.9038 | 180 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Restore lost internet connection | Corrective | Monitoring | 0 | 0 | 0 | N/A | Site | Network/IT | 33.25 | 20 | 3 | Interval | 1 | 1 | 0 | 33.25 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Excavate and replace failed foundation element | Corrective | PV Array | 0 |  |  | N/A |  | Structural engineer | 40.4519 | 25 | 3 | Weibull | 103.0445 | 4 | 400 | 16673.3922 | 41217.7986 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair roof leaks | Corrective | Roof | 0 |  |  | N/A | acres | Roofing | 16.4519 | 25 | 1 | Weibull | 2.3153 | 8 | 400 | 304.7263 | 926.1115 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-roof (new roof) | Corrective | Roof | 0 |  |  | N/A | acres | Roofing | 16.4519 | 30 | 4 | Weibull | 2.3153 | 24 | 75000 | 914.1789 | 173645.9016 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair/replace tracker drive shaft | Corrective | Tracker | 0 |  |  | N/A | row | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 0.5 | 120 | 1093.857 | 12365.3396 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace hydraulic cylinder | Corrective | Tracker | 0 |  |  | N/A |  | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 0.5 | 120 | 1093.857 | 12365.3396 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracker drive bearing | Corrective | Tracker | 0 |  |  | N/A | row | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 0.5 | 40 | 1093.857 | 4121.7799 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracker motor controller | Corrective | Tracker | 0 |  |  | N/A |  | Journeyman electrician | 14.4231 | 25 | 3 | Weibull | 103.0445 | 0.5 | 250 | 743.1093 | 25761.1241 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracker mount bearing | Corrective | Tracker | 0 |  |  | N/A |  | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 0.5 | 40 | 1093.857 | 4121.7799 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace/upgrade tracker control software | Corrective | Tracker | 0 |  |  | N/A |  | Network/IT | 33.25 | 25 | 3 | Weibull | 103.0445 | 1 | 0 | 3426.2295 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace transformer | Corrective | Transformer | 0 | 0 | 0 | N/A | Transformer | Master electrician | 23.1971 | 50 | 2 | Weibull | 1 | 4 | 22000 | 92.7885 | 22000 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-tap transformer | Corrective | Transformer | 0 | 0 | 0 | N/A | Transformer | Master electrician | 23.1971 | 25 | 3 | Weibull | 1 | 2 | 0 | 46.3942 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manage inventory of spare parts | Administration | Asset Management | 0 | 1 | 1 | Monitoring |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Confirm availability and take any measures to secure operating instructions, warranties and performance guarantees, and other project documentation. | Administration | Documents | 0 |  |  | N/A |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Document all O&M activities in a workbook available to all service personnel. | Administration | Documents | 0 |  |  | N/A |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Review O&M agreements and ensure that services are actually provided | Administration | Documents | 0 |  |  | N/A |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Update record with preventative maintenance activities and track any problems or warranty issues and secure the record on-site. | Administration | Documents | 0 |  |  | N/A |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maintain a log of cumulative power delivery (kWh to date) and chart this value against date. Chart the value even for uneven or infrequent intervals. Explain variation by season or weather. | Administration | Meter | 0 |  |  | N/A |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 0.5 | 0 | 8.3317 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meet with key site staff to continue awareness, question any issues, and report on findings. | Administration | Documents | 0 |  |  | N/A |  | Administrator | 16.6635 | 1 | 1 | interval | 1 | 2 | 0 | 33.3269 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 4816.4973 | 34158.352 | 100% | 27.5345 | 28.0109 | 28.4983 | 28.9969 | 29.5069 | 109.607 | 111.732 | 113.9008 | 116.1143 | 118.3734 | 8702.3079 | 8829.9577 | 8985.1983 | 9165.7488 | 9369.4077 | 9594.0452 | 9837.5957 | 10098.0514 | 10373.4564 | 10661.9018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Ground-Mount Details
Ground Mount (> 100kW)
Inputs |  |  | Lifetime NPV by Service Type |  |  |  |  | Lifetime NPV by Component Type
Analysis Period (Project Life) | 20 |  | Service | Avg. Cost/Yr | NPV (Life) | % of Total |  | Component | Avg. Cost/Yr | NPV (Life) | % of Total
Discount Rate | 7% |  | Administrator | 1335.0497 | 13078.6194 | 9.493% |  | Documents | 815.6273 | 8271.3287 | 6.085%
Inflation Rate | 2% |  | Cleaner | 807.8295 | 8192.2507 | 5.946% |  | Asset Management | 251.5156 | 2124.5203 | 1.563%
Truck Rental Cost/ day | 100 |  | Inverter specialist | 3271.3815 | 24030.4039 | 17.44% |  | PV Array | 2967.0034 | 23813.4279 | 17.52%
Working Hours/year | 2080 |  | Inspector | 1763.2589 | 17874.0771 | 12.97% |  | Cleaning/Veg | 1547.7311 | 15695.6397 | 11.55%
System Size (Wp DC) | 440000 |  | Journeyman electrician | 4258.2291 | 31674.1499 | 22.99% |  | Electrical | 416.7669 | 3660.6886 | 2.693%
Energy Yield (kWh/kWp/year) | 1596 |  | PV module/array Specialist | 1257.5467 | 10753.8019 | 7.805% |  | Meter | 0 | 0 | 0%
Module Power (W STC) | 305 |  | Network/IT | 145.9282 | 1294.445 | 0.9395% |  | PV Module | 4531.6551 | 34244.4307 | 25.19%
Number of Modules | 1443 |  | Master electrician | 432.2165 | 3658.5181 | 2.655% |  | DC Wiring | 1735.4148 | 14725.0595 | 10.83%
Module Type/ Degradation | Mulit-crystal Silicon:0.64%/year |  | Mechanic | 871.9334 | 5840.0329 | 4.239% |  | Mechanical | 733.5631 | 7321.1813 | 5.386%
Module Encapsulant | Ethyl Vinyl Acetate (EVA) |  | Designer | 0 | 0 | 0% |  | AC Wiring | 153.2395 | 1590.761 | 1.17%
Modules per String | 14 |  | Pest control | 146.1662 | 1482.2804 | 1.076% |  | Inverter | 3302.2265 | 24461.5826 | 18%
Number of Strings | 103.0445 |  | Roofing | 0 | 0 | 0% |  | Monitoring | 2.4704 | 12.7679 | 0.009394%
Strings per Combiner Box | 6 |  | Structural engineer | 1648.3766 | 12353.7495 | 8.966% |  | Total | 16457.2138 | 135921.3882 | 100%
Number of Combiner Boxes | 18 |  | Mower/Trimmer | 741.2247 | 7516.8074 | 5.456%
Combiner boxes per DC disconnect | 1 |  | Utilities locator | 3.315 | 29.1498 | 0.02116%
Number of DC Disconnects | 18 |  | Total | 16682.456 | 137778.286 | 100%
Inverter Type | String Inverter
Inverter Warranty (years) | 10
Number of Inverters | 1
Inverter Capacity (kWp) | 400
Number of Transformers | 1
Detailed Measures | [21 empty] | Annual Cash Flow
Activity Description | Activity Type | Component Type | Applicable ? (1= yes, 0 = no) | Covered by Warranty - Materials (1=yes, 0=no) | Covered by Warranty - Labor (1=yes, 0=no) | Warranty or Service Package Type | Applicable Unit | Service Category | Labor Rate per Hour | Mean Interval (years) | Weibull or Lognormal Shape Factor | Type of Distribution | Approx. Number of Units | Labor hrs per unit | Material/ Other Cost per unit | Total Labor Cost | Total Matl and Other Cost | Total Cost for Measure | Notes | Reference | Average Annual Expense | NPV (Project Life) | % of Total NPV | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
Monitoring annual service package | Preventive | Asset Management | 1 | 1 | 1 | Monitoring | System | Administrator | 0 | 1 | 1 | interval | 1 | 0 | 50 | 0 | 50 | 50 |  |  | 48.688 | 411.2613 | 0.2985% | 0 | 0 | 0 | 0 | 0 | 56.3081 | 57.4343 | 58.583 | 59.7546 | 60.9497 | 62.1687 | 63.4121 | 64.6803 | 65.9739 | 67.2934 | 68.6393 | 70.0121 | 71.4123 | 72.8406 | 74.2974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter inspection | Preventive | Electrical | 1 | 0 | 0 | N/A | Inverter | Inspector | 25.1731 | 1 | 1 | interval | 1 | 1 | 0 | 25.1731 | 0 | 25.1731 |  |  | 31.1936 | 316.3365 | 0.2296% | 25.6765 | 26.1901 | 26.7139 | 27.2481 | 27.7931 | 28.349 | 28.916 | 29.4943 | 30.0842 | 30.6858 | 31.2996 | 31.9255 | 32.5641 | 33.2153 | 33.8796 | 34.5572 | 35.2484 | 35.9534 | 36.6724 | 37.4059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrical labor mobilization | Preventive | Electrical | 1 | 1 | 1 | EPC | Site | Master electrician | 23.1971 | 1 | 1 | interval | 1 | 1 | 0 | 23.1971 | 0 | 23.1971 |  |  | 15.791 | 111.5278 | 0.08095% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.8427 | 29.4196 | 30.0079 | 30.6081 | 31.2203 | 31.8447 | 32.4816 | 33.1312 | 33.7938 | 34.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check position of disconnect switches and breakers. | Preventive | AC Wiring | 1 | 0 | 0 | N/A | Disconnect Box | Inspector | 25.1731 | 1 | 1 | interval | 18 | 0.08 | 0 | 36.2492 | 0 | 36.2492 |  |  | 44.9188 | 455.5245 | 0.3306% | 36.9742 | 37.7137 | 38.468 | 39.2373 | 40.0221 | 40.8225 | 41.639 | 42.4718 | 43.3212 | 44.1876 | 45.0714 | 45.9728 | 46.8922 | 47.8301 | 48.7867 | 49.7624 | 50.7577 | 51.7728 | 52.8083 | 53.8645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect electrical boxes for corrosion or intrusion of water or insects. Seal boxes if required. | Preventive | AC Wiring | 1 | 0 | 0 | N/A | Combiner Box | Inspector | 25.1731 | 1 | 1 | interval | 18 | 0.08 | 0 | 36.2492 | 0 | 36.2492 |  |  | 44.9188 | 455.5245 | 0.3306% | 36.9742 | 37.7137 | 38.468 | 39.2373 | 40.0221 | 40.8225 | 41.639 | 42.4718 | 43.3212 | 44.1876 | 45.0714 | 45.9728 | 46.8922 | 47.8301 | 48.7867 | 49.7624 | 50.7577 | 51.7728 | 52.8083 | 53.8645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check proper position of DC disconnect switches. | Preventive | DC Wiring | 1 | 0 | 0 | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 18 | 0.08 | 0 | 36.2492 | 0 | 36.2492 |  |  | 44.9188 | 455.5245 | 0.3306% | 36.9742 | 37.7137 | 38.468 | 39.2373 | 40.0221 | 40.8225 | 41.639 | 42.4718 | 43.3212 | 44.1876 | 45.0714 | 45.9728 | 46.8922 | 47.8301 | 48.7867 | 49.7624 | 50.7577 | 51.7728 | 52.8083 | 53.8645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DC circuit test & combiner box inspection | Preventive | Electrical | 1 | 0 | 0 | N/A | Combiner Box | PV module/array Specialist | 24.0385 | 1 | 1 | interval | 18 | 0.083333 | 0 | 36.0577 | 0 | 36.0577 |  |  | 44.6815 | 453.1176 | 0.3289% | 36.7788 | 37.5144 | 38.2647 | 39.03 | 39.8106 | 40.6068 | 41.419 | 42.2473 | 43.0923 | 43.9541 | 44.8332 | 45.7299 | 46.6445 | 47.5774 | 48.5289 | 49.4995 | 50.4895 | 51.4993 | 52.5292 | 53.5798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV module torque check & visual inspection | Preventive | Mechanical | 1 | 0 | 0 | N/A | Rail/ Fastener | PV module/array Specialist | 24.0385 | 5 | 1 | interval | 1648.7119 | 0.0083333 | 0 | 330.2708 | 0 | 330.2708 |  |  | 85.1255 | 752.5785 | 0.5462% | 0 | 0 | 0 | 0 | 364.6457 | 0 | 0 | 0 | 0 | 402.5983 | 0 | 0 | 0 | 0 | 444.501 | 0 | 0 | 0 | 0 | 490.7651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV module electrical connection check | Preventive | Electrical | 1 | 0 | 0 | N/A | PV Module | PV module/array Specialist | 24.0385 | 5 | 1 | Interval | 1442.623 | 0.0041667 | 0 | 144.4935 | 0 | 144.4935 |  |  | 37.2424 | 329.2531 | 0.239% | 0 | 0 | 0 | 0 | 159.5325 | 0 | 0 | 0 | 0 | 176.1368 | 0 | 0 | 0 | 0 | 194.4692 | 0 | 0 | 0 | 0 | 214.7097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Racking torque check & inspection | Preventive | Mechanical | 1 | 0 | 0 | N/A | Structure | Inspector | 25.1731 | 5 | 1 | interval | 103.0445 | 0.0083333 | 0 | 21.6162 | 0 | 21.6162 |  |  | 5.5715 | 49.2563 | 0.03575% | 0 | 0 | 0 | 0 | 23.8661 | 0 | 0 | 0 | 0 | 26.3501 | 0 | 0 | 0 | 0 | 29.0926 | 0 | 0 | 0 | 0 | 32.1206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check grounding hardware | Preventive | Electrical | 1 | 0 | 0 | N/A | Structure | Master electrician | 23.1971 | 1 | 1 | interval | 1 | 0.00055556 | 0 | 0.012887 | 0 | 0.012887 |  |  | 0.015969 | 0.16195 | 0.0001175% | 0.013145 | 0.013408 | 0.013676 | 0.01395 | 0.014229 | 0.014513 | 0.014803 | 0.0151 | 0.015402 | 0.01571 | 0.016024 | 0.016344 | 0.016671 | 0.017005 | 0.017345 | 0.017691 | 0.018045 | 0.018406 | 0.018774 | 0.01915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor available by email and phone 24x7x365 | Preventive | PV Array | 1 | 0 | 0 | N/A |  | Administrator | 16.6635 | 1 | 1 | interval | 1 | 12 | 0 | 199.9615 | 0 | 199.9615 |  |  | 247.7855 | 2512.8087 | 1.824% | 203.9608 | 208.04 | 212.2008 | 216.4448 | 220.7737 | 225.1892 | 229.693 | 234.2868 | 238.9725 | 243.752 | 248.627 | 253.5996 | 258.6716 | 263.845 | 269.1219 | 274.5043 | 279.9944 | 285.5943 | 291.3062 | 297.1323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Install software updates, inverter and other | Preventive | Electrical | 1 | 1 | 1 | EPC | NCU | Inverter specialist | 24.0385 | 5 | 1 | interval | 1 | 1 | 500 | 24.0385 | 500 | 524.0385 |  |  | 74.199 | 456.8576 | 0.3316% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705.2868 | 0 | 0 | 0 | 0 | 778.6936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check central SCADA/network manager | Preventive | Electrical | 1 | 0 | 0 | N/A | NCU | Network/IT | 33.25 | 1 | 1 | interval | 1 | 0.25 | 0 | 8.3125 | 0 | 8.3125 |  |  | 10.3006 | 104.4587 | 0.07582% | 8.4787 | 8.6483 | 8.8213 | 8.9977 | 9.1777 | 9.3612 | 9.5484 | 9.7394 | 9.9342 | 10.1329 | 10.3355 | 10.5423 | 10.7531 | 10.9682 | 11.1875 | 11.4113 | 11.6395 | 11.8723 | 12.1097 | 12.3519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Corrosion inpsection | Preventive | Mechanical | 1 | 0 | 0 | N/A | connection | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 259.3947 |  |  | 321.4331 | 3259.6732 | 2.366% | 264.5826 | 269.8742 | 275.2717 | 280.7772 | 286.3927 | 292.1206 | 297.963 | 303.9222 | 310.0007 | 316.2007 | 322.5247 | 328.9752 | 335.5547 | 342.2658 | 349.1111 | 356.0933 | 363.2152 | 370.4795 | 377.8891 | 385.4469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Galvanazation inspection | Preventive | Mechanical | 1 | 0 | 0 | N/A | connection | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 259.3947 |  |  | 321.4331 | 3259.6732 | 2.366% | 264.5826 | 269.8742 | 275.2717 | 280.7772 | 286.3927 | 292.1206 | 297.963 | 303.9222 | 310.0007 | 316.2007 | 322.5247 | 328.9752 | 335.5547 | 342.2658 | 349.1111 | 356.0933 | 363.2152 | 370.4795 | 377.8891 | 385.4469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Use infrared camera to inspect for hot spots; bypass diode failure | Preventive | PV Module | 1 | 0 | 0 | N/A | strings | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.15 | 0 | 389.0921 | 0 | 389.0921 |  |  | 482.1496 | 4889.5099 | 3.549% | 396.8739 | 404.8114 | 412.9076 | 421.1658 | 429.5891 | 438.1809 | 446.9445 | 455.8834 | 465.001 | 474.301 | 483.7871 | 493.4628 | 503.3321 | 513.3987 | 523.6667 | 534.14 | 544.8228 | 555.7193 | 566.8337 | 578.1703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-torque all electrical connections on AC side of system. | Preventive | AC Wiring | 1 | 0 | 0 | N/A |  | Journeyman electrician | 14.4231 | 1 | 1 | interval | 1 | 0.5 | 0 | 7.2115 | 0 | 7.2115 |  |  | 8.9363 | 90.6235 | 0.06577% | 7.3558 | 7.5029 | 7.6529 | 7.806 | 7.9621 | 8.1214 | 8.2838 | 8.4495 | 8.6185 | 8.7908 | 8.9666 | 9.146 | 9.3289 | 9.5155 | 9.7058 | 9.8999 | 10.0979 | 10.2999 | 10.5058 | 10.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test open circuit voltage or IV curve of series strings of modules | Preventive | PV Array | 1 | 0 | 0 | N/A | strings | PV module/array Specialist | 24.0385 | 1 | 1 | interval | 103.0445 | 0.15 | 0 | 371.5547 | 0 | 371.5547 |  |  | 460.4179 | 4669.1271 | 3.389% | 378.9858 | 386.5655 | 394.2968 | 402.1827 | 410.2264 | 418.4309 | 426.7995 | 435.3355 | 444.0422 | 452.9231 | 461.9815 | 471.2212 | 480.6456 | 490.2585 | 500.0637 | 510.0649 | 520.2662 | 530.6716 | 541.285 | 552.1107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AC disconnect box inspection | Preventive | Electrical | 1 | 0 | 0 | N/A | Disconnect Box | Inspector | 25.1731 | 1 | 1 | interval | 1 | 0.25 | 0 | 6.2933 | 0 | 6.2933 |  |  | 7.7984 | 79.0841 | 0.0574% | 6.4191 | 6.5475 | 6.6785 | 6.812 | 6.9483 | 7.0872 | 7.229 | 7.3736 | 7.521 | 7.6715 | 7.8249 | 7.9814 | 8.141 | 8.3038 | 8.4699 | 8.6393 | 8.8121 | 8.9883 | 9.1681 | 9.3515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect cabling for signs of cracks, defects, pulling out of connections; overheating, arcing, short or open circuits, ground faults in wiring and condition of wire insulation and protective materials.. | Preventive | DC Wiring | 1 | 0 | 0 | N/A | strings | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 259.3947 |  |  | 321.4331 | 3259.6732 | 2.366% | 264.5826 | 269.8742 | 275.2717 | 280.7772 | 286.3927 | 292.1206 | 297.963 | 303.9222 | 310.0007 | 316.2007 | 322.5247 | 328.9752 | 335.5547 | 342.2658 | 349.1111 | 356.0933 | 363.2152 | 370.4795 | 377.8891 | 385.4469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test modules showing corrosion of ribbons to junction box | Preventive | PV Module | 1 | 0 | 0 | N/A | modules | Journeyman electrician | 14.4231 | 5 | 1 | interval | 1443 | 0.08 | 0 | 1665 | 0 | 1665 |  |  | 429.1447 | 3793.9872 | 2.754% | 0 | 0 | 0 | 0 | 1838.2945 | 0 | 0 | 0 | 0 | 2029.6257 | 0 | 0 | 0 | 0 | 2240.8708 | 0 | 0 | 0 | 0 | 2474.1024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test output of modules that exhibit cracked glass, bubble formation oxidation of busbars, discoloration of busbars, or PV module hot spots (bypass diode failure) | Preventive | PV Module | 1 | 0 | 0 | N/A | modules | Journeyman electrician | 14.4231 | 5 | 1 | interval | 1443 | 0.08 | 0 | 1665 | 0 | 1665 |  |  | 429.1447 | 3793.9872 | 2.754% | 0 | 0 | 0 | 0 | 1838.2945 | 0 | 0 | 0 | 0 | 2029.6257 | 0 | 0 | 0 | 0 | 2240.8708 | 0 | 0 | 0 | 0 | 2474.1024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exercise operation of all protection devices. | Preventive | AC Wiring | 1 | 0 | 0 | N/A |  | Journeyman electrician | 14.4231 | 1 | 1 | interval | 2 | 0.08 | 0 | 2.3077 | 0 | 2.3077 |  |  | 2.8596 | 28.9995 | 0.02105% | 2.3538 | 2.4009 | 2.4489 | 2.4979 | 2.5479 | 2.5988 | 2.6508 | 2.7038 | 2.7579 | 2.8131 | 2.8693 | 2.9267 | 2.9852 | 3.045 | 3.1059 | 3.168 | 3.2313 | 3.296 | 3.3619 | 3.4291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Array cleaning | Preventive | Cleaning/Veg | 1 | 0 | 0 | N/A | Acre | Cleaner | 10.6779 | 0.25 | 1 | interval | 1 | 4 | 120 | 42.7115 | 120 | 162.7115 | 2 gal fuel/acre @$4/gal + 500 gal H2O/acre @$0.40/gal |  | 806.5063 | 8178.8324 | 5.936% | 663.8631 | 677.1403 | 690.6831 | 704.4968 | 718.5867 | 732.9585 | 747.6176 | 762.57 | 777.8214 | 793.3778 | 809.2454 | 825.4303 | 841.9389 | 858.7777 | 875.9532 | 893.4723 | 911.3417 | 929.5686 | 948.1599 | 967.1231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
General Cleaning/Veg Mobilization | Preventive | Cleaning/Veg | 1 | 0 | 0 | N/A | Site | Mower/Trimmer | 21.2308 | 1 | 1 | interval | 1 | 4 | 120 | 84.9231 | 120 | 204.9231 | Other cost = water truckr rental |  | 253.9337 | 2575.1577 | 1.869% | 209.0215 | 213.202 | 217.466 | 221.8153 | 226.2516 | 230.7767 | 235.3922 | 240.1 | 244.902 | 249.8001 | 254.7961 | 259.892 | 265.0899 | 270.3916 | 275.7995 | 281.3155 | 286.9418 | 292.6806 | 298.5342 | 304.5049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation management (mowing, trimming) per acre | Preventive | Cleaning/Veg | 1 | 0 | 0 | N/A | Acre | Mower/Trimmer | 21.2308 | 0.25 | 1 | interval | 2.3153 | 2 | 0 | 98.3103 | 0 | 98.3103 | Other cost = 1 gal fuel/acre @ $4/gal + $10/acre mowing consumables |  | 487.291 | 4941.6497 | 3.587% | 401.106 | 409.1281 | 417.3107 | 425.6569 | 434.17 | 442.8534 | 451.7105 | 460.7447 | 469.9596 | 479.3588 | 488.946 | 498.7249 | 508.6994 | 518.8734 | 529.2509 | 539.8359 | 550.6326 | 561.6452 | 572.8781 | 584.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Look for any signs of intrusion by pests such as insects and rodents. Remove any nests from electrical boxes (junction boxes, pull boxes, combiner boxes) or around the array. Use safe sanitation practices because pests may carry disease. | Preventive | DC Wiring | 1 | 0 | 0 | N/A |  | Pest control | 14.5865 | 1 | 1 | interval | 37 | 0.15 | 1 | 80.9553 | 37 | 117.9553 |  |  | 146.1662 | 1482.2804 | 1.076% | 120.3144 | 122.7207 | 125.1751 | 127.6786 | 130.2322 | 132.8368 | 135.4935 | 138.2034 | 140.9675 | 143.7868 | 146.6626 | 149.5958 | 152.5877 | 155.6395 | 158.7523 | 161.9273 | 165.1659 | 168.4692 | 171.8386 | 175.2754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Open each combiner box and check that no fuses have blown and that all electrical connections are tight. Use an infrared camera for identifying loose connections because they are warmer than good connections when passing current. | Preventive | DC Wiring | 1 | 0 | 0 | N/A | Combiner Box | Journeyman electrician | 14.4231 | 1 | 1 | interval | 18 | 0.15 | 0 | 38.9423 | 0 | 38.9423 |  |  | 48.256 | 489.367 | 0.3552% | 39.7212 | 40.5156 | 41.3259 | 42.1524 | 42.9955 | 43.8554 | 44.7325 | 45.6271 | 46.5397 | 47.4705 | 48.4199 | 49.3883 | 50.376 | 51.3835 | 52.4112 | 53.4594 | 54.5286 | 55.6192 | 56.7316 | 57.8662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-torque all electrical connections in combiner box. | Preventive | DC Wiring | 1 | 0 | 0 | N/A | Combiner Box | Journeyman electrician | 14.4231 | 1 | 1 | interval | 18 | 0.25 | 0 | 64.9038 | 0 | 64.9038 |  |  | 80.4266 | 815.6116 | 0.592% | 66.2019 | 67.526 | 68.8765 | 70.254 | 71.6591 | 73.0923 | 74.5541 | 76.0452 | 77.5661 | 79.1174 | 80.6998 | 82.3138 | 83.96 | 85.6392 | 87.352 | 89.0991 | 90.8811 | 92.6987 | 94.5526 | 96.4437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test system grounding with "megger" | Preventive | DC Wiring | 1 | 0 | 0 | N/A | strings | Master electrician | 23.1971 | 5 | 1 | interval | 103.0445 | 0.25 | 0 | 597.5838 | 0 | 597.5838 |  |  | 154.024 | 1361.6968 | 0.9883% | 0 | 0 | 0 | 0 | 659.7808 | 0 | 0 | 0 | 0 | 728.4513 | 0 | 0 | 0 | 0 | 804.2691 | 0 | 0 | 0 | 0 | 887.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Calibrate or replace weather sensors & meters | Preventive | Electrical | 1 | 0 | 0 | N/A | Weather Station | Network/IT | 33.25 | 5 | 1 | interval | 1 | 0.5 | 500 | 16.625 | 500 | 516.625 |  |  | 133.1573 | 1177.2184 | 0.8544% | 0 | 0 | 0 | 0 | 570.3957 | 0 | 0 | 0 | 0 | 629.763 | 0 | 0 | 0 | 0 | 695.3092 | 0 | 0 | 0 | 0 | 767.6776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check Electrical connections & enclosure for tracking motor/controller | Preventive | Tracker | 0 | 0 | 0 | N/A | Controller | Inspector | 25.1731 | 1 | 1 | interval | 1 | 0.083333 | 0 | 2.0978 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check Electrical connections (motor) | Preventive | Tracker | 0 | 0 | 0 | N/A | Motor | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.083333 | 0 | 216.1623 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transformer/switchgear inspection | Preventive | Electrical | 1 | 0 | 0 | N/A | Transformer | Inspector | 25.1731 | 1 | 1 | interval | 1 | 2 | 0 | 50.3462 | 0 | 50.3462 |  |  | 62.3872 | 632.6729 | 0.4592% | 51.3531 | 52.3801 | 53.4277 | 54.4963 | 55.5862 | 56.6979 | 57.8319 | 58.9885 | 60.1683 | 61.3717 | 62.5991 | 63.8511 | 65.1281 | 66.4307 | 67.7593 | 69.1145 | 70.4968 | 71.9067 | 73.3448 | 74.8117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Clean (vacuum) dust from heat rejection fins | Preventive | Inverter | 1 | 0 | 0 | N/A | inverter | Cleaner | 10.6779 | 1 | 1 | interval | 1 | 0.1 | 0 | 1.0678 | 0 | 1.0678 |  |  | 1.3232 | 13.4183 | 0.009739% | 1.0891 | 1.1109 | 1.1331 | 1.1558 | 1.1789 | 1.2025 | 1.2266 | 1.2511 | 1.2761 | 1.3016 | 1.3277 | 1.3542 | 1.3813 | 1.4089 | 1.4371 | 1.4658 | 1.4952 | 1.5251 | 1.5556 | 1.5867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Performance test: measure incident light while observing temp and energy output. Calculate PV module efficiency as a function of temp and calculate BOS efficiency. Compare readings with diagnostic benchmark (original efficiency of system). | Preventive | Inverter | 1 | 0 |  | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 1 | 1 | 0 | 25.1731 | 0 | 25.1731 |  |  | 31.1936 | 316.3365 | 0.2296% | 25.6765 | 26.1901 | 26.7139 | 27.2481 | 27.7931 | 28.349 | 28.916 | 29.4943 | 30.0842 | 30.6858 | 31.2996 | 31.9255 | 32.5641 | 33.2153 | 33.8796 | 34.5572 | 35.2484 | 35.9534 | 36.6724 | 37.4059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace any air filters on air-cooled equipment such as inverter. | Preventive | Inverter | 1 | 0 | 0 | N/A | inverter | Inverter specialist | 24.0385 | 1 | 1 | interval | 1 | 0.25 | 25 | 6.0096 | 25 | 31.0096 |  |  | 38.4261 | 389.6811 | 0.2828% | 31.6298 | 32.2624 | 32.9077 | 33.5658 | 34.2371 | 34.9219 | 35.6203 | 36.3327 | 37.0594 | 37.8005 | 38.5566 | 39.3277 | 40.1142 | 40.9165 | 41.7349 | 42.5696 | 43.4209 | 44.2894 | 45.1752 | 46.0787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace transient voltage surge suppression devices | Preventive | Inverter | 1 | 0 | 0 | Inverter |  | Master electrician | 23.1971 | 5 | 1 | interval | 1 | 0.5 | 105 | 11.5986 | 105 | 116.5986 |  |  | 30.0526 | 265.6897 | 0.1928% | 0 | 0 | 0 | 0 | 128.7342 | 0 | 0 | 0 | 0 | 142.133 | 0 | 0 | 0 | 0 | 156.9263 | 0 | 0 | 0 | 0 | 173.2593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test overvoltage surge suppressors in inverter | Preventive | Inverter | 1 | 0 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 5 | 1 | interval | 1 | 0.1 | 0 | 2.4038 | 0 | 2.4038 |  |  | 0.61958 | 5.4776 | 0.003976% | 0 | 0 | 0 | 0 | 2.654 | 0 | 0 | 0 | 0 | 2.9303 | 0 | 0 | 0 | 0 | 3.2353 | 0 | 0 | 0 | 0 | 3.572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter | Corrective | Inverter | 1 | 1 | 1 | Inverter | Inverter | Inverter specialist | 24.0385 | 10 | 1 | Weibull | 1 | 0 | 80300 | 0 | 80300 | 80300 | $300 flat fee |  | 1189.3017 | 8869.1204 | 6.437% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3323.4833 | 3067.3563 | 2830.9679 | 2612.797 | 2411.4397 | 2225.6001 | 2054.0823 | 1895.7828 | 1749.6827 | 1614.8419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace modules failing performance test or IR scan | Corrective | PV module | 1 | 1 | 1 | Module (Product) | modules | Journeyman electrician | 14.4231 | 50 | 2 | Weibull | 1443 | 0.15 | 244 | 3121.875 | 352092 | 355213.875 |  |  | 2721.5633 | 18665.2308 | 13.55% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3703.0078 | 4082.7036 | 4466.4984 | 4853.5741 | 5243.0891 | 5634.1822 | 6025.9748 | 6417.5748 | 6808.08 | 7196.5811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dispatch contractor in response to alarms, alerts, or contact by others | Corrective | PV Array | 1 | 1 | 1 | Monitoring |  | Administrator | 16.6635 | 1 | 1 | Interval | 1 | 1 | 4 | 16.6635 | 4 | 20.6635 |  |  | 20.1212 | 169.9616 | 0.1234% | 0 | 0 | 0 | 0 | 0 | 23.2704 | 23.7358 | 24.2105 | 24.6947 | 25.1886 | 25.6924 | 26.2063 | 26.7304 | 27.265 | 27.8103 | 28.3665 | 28.9338 | 29.5125 | 30.1028 | 30.7048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace MC connector lead to combiner box | Corrective | DC wiring | 1 | 1 | 1 | Module (Product) | modules | PV module/array Specialist | 24.0385 | 25 | 1 | Weibull | 1443 | 0.1 | 20 | 3468.75 | 28860 | 32328.75 |  |  | 473.5758 | 3419.6325 | 2.482% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1035.5265 | 1014.8214 | 994.5303 | 974.6449 | 955.1571 | 936.0589 | 917.3426 | 899.0006 | 881.0253 | 863.4094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Start/stop inverter (reboot to clear unknown error) | Corrective | Inverter | 1 | 0 | 0 | EPC | inverter | Inspector | 25.1731 | 1 | 3 | Interval | 1 | 0.25 | 0 | 6.2933 | 0 | 6.2933 |  |  | 7.7984 | 79.0841 | 0.0574% | 6.4191 | 6.5475 | 6.6785 | 6.812 | 6.9483 | 7.0872 | 7.229 | 7.3736 | 7.521 | 7.6715 | 7.8249 | 7.9814 | 8.141 | 8.3038 | 8.4699 | 8.6393 | 8.8121 | 8.9883 | 9.1681 | 9.3515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter fan motor | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 15 | 1 | Weibull | 1 | 1 | 120 | 24.0385 | 120 | 144.0385 |  |  | 2.3432 | 17.1677 | 0.01246% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7346 | 5.4721 | 5.2216 | 4.9825 | 4.7544 | 4.5367 | 4.329 | 4.1308 | 3.9417 | 3.7612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace MC Connectors between modules | Corrective | DC wiring | 1 | 1 | 1 | Module (Product) | modules | PV module/array Specialist | 24.0385 | 25 | 1 | Weibull | 1443 | 0.1 | 5 | 3468.75 | 7215 | 10683.75 |  |  | 156.5036 | 1130.0931 | 0.8202% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342.2126 | 335.3702 | 328.6645 | 322.0929 | 315.6528 | 309.3414 | 303.1561 | 297.0946 | 291.1543 | 285.3327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate ground fault | Corrective | DC Wiring | 1 | 1 | 1 | EPC |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 1 | 4 | 0 | 92.7885 | 0 | 92.7885 |  |  | 1.3592 | 9.8149 | 0.007124% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9721 | 2.9127 | 2.8545 | 2.7974 | 2.7414 | 2.6866 | 2.6329 | 2.5803 | 2.5287 | 2.4781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair or replace damage to module frame | Corrective | PV module | 1 | 1 | 1 | Module (Product) | modules | Mechanic | 21.2308 | 50 | 3 | Weibull | 1443 | 0.25 | 50 | 7659 | 72150 | 79809 |  |  | 317.7421 | 2098.4555 | 1.523% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285.1189 | 345.0039 | 411.4517 | 484.6051 | 564.5758 | 651.4407 | 745.2369 | 845.9579 | 953.5489 | 1067.9027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace protective devices (breakers) in building panel | Corrective | AC wiring | 1 | 1 | 1 | N/A |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 3 | 0.25 | 10 | 17.3978 | 30 | 47.3978 |  |  | 1.544 | 17.0835 | 0.0124% | 1.858 | 1.8209 | 1.7844 | 1.7488 | 1.7138 | 1.6795 | 1.646 | 1.613 | 1.5808 | 1.5492 | 1.5182 | 1.4879 | 1.4581 | 1.4289 | 1.4004 | 1.3724 | 1.3449 | 1.318 | 1.2917 | 1.2659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair ground fault | Corrective | DC Wiring | 1 | 1 | 1 | EPC |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 1 | 1 | 20 | 23.1971 | 20 | 43.1971 |  |  | 0.63278 | 4.5693 | 0.003316% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3837 | 1.356 | 1.3289 | 1.3023 | 1.2763 | 1.2507 | 1.2257 | 1.2012 | 1.1772 | 1.1537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter AC fuse(s) | Corrective | AC wiring | 1 | 1 | 1 | EPC |  | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 3 | 0.15 | 10 | 6.4904 | 30 | 36.4904 |  |  | 0.53454 | 3.8598 | 0.002801% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1688 | 1.1455 | 1.1226 | 1.1001 | 1.0781 | 1.0566 | 1.0354 | 1.0147 | 0.99444 | 0.97455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair cracking of PV module back sheet | Corrective | PV module | 1 | 1 | 1 | Module (Product) | modules | Journeyman electrician | 14.4231 | 50 | 3 | Weibull | 1443 | 0.1 | 25 | 2081.25 | 36075 | 38156.25 |  |  | 151.9108 | 1003.2602 | 0.7282% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136.3138 | 164.9445 | 196.7128 | 231.6871 | 269.9206 | 311.4502 | 356.2937 | 404.4479 | 455.8866 | 510.5585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair or replace rack parts damaged by corrosion or physical damage | Corrective | PV Array | 1 | 1 | 1 | EPC |  | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 1 | 200 | 2187.7139 | 20608.8993 | 22796.6132 |  |  | 554.1912 | 3741.5775 | 2.716% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604.7333 | 715.6598 | 831.3717 | 949.6443 | 1067.9454 | 1183.4954 | 1293.3505 | 1394.5051 | 1484.0112 | 1559.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace fuse(s) on DC source circuits to inverter | Corrective | DC wiring | 1 | 1 | 1 | EPC |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 18 | 0.08 | 5 | 33.4038 | 90 | 123.4038 |  |  | 1.8077 | 13.0533 | 0.009474% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9528 | 3.8737 | 3.7963 | 3.7204 | 3.646 | 3.5731 | 3.5016 | 3.4316 | 3.363 | 3.2958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
manual reset of arc-fault trip (NEC 690.11) | Corrective | Inverter | 1 | 1 | 1 | EPC | inverter | Inverter specialist | 24.0385 | 25 | 1 | Weibull | 1 | 0.08 | 0 | 1.9231 | 0 | 1.9231 |  |  | 0.028171 | 0.20342 | 0.0001476% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061598 | 0.060367 | 0.05916 | 0.057977 | 0.056818 | 0.055682 | 0.054568 | 0.053477 | 0.052408 | 0.05136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seal Leaking Junction Box | Corrective | DC Wiring | 1 | 1 | 1 | Module (Product) | modules | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 1443 | 0.25 | 10 | 5203.125 | 14430 | 19633.125 |  |  | 287.6008 | 2076.7296 | 1.507% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 628.8712 | 616.2971 | 603.9744 | 591.8981 | 580.0632 | 568.465 | 557.0986 | 545.9596 | 535.0432 | 524.3452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate line-to-line fault | Corrective | AC Wiring | 1 | 1 | 1 | EPC |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 1 | 1 | 0 | 23.1971 | 0 | 23.1971 |  |  | 0.33981 | 2.4537 | 0.001781% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74303 | 0.72817 | 0.71361 | 0.69934 | 0.68536 | 0.67166 | 0.65823 | 0.64507 | 0.63217 | 0.61953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate underground AC wiring | Corrective | AC Wiring | 1 | 1 | 1 | N/A |  | Utilities locator | 18.5144 | 25 | 3 | Weibull | 1 | 4 | 0 | 74.0577 | 0 | 74.0577 |  |  | 2.1087 | 15.8036 | 0.01147% | 0.014503 | 0.059144 | 0.13557 | 0.24525 | 0.38935 | 0.56855 | 0.78295 | 1.0319 | 1.3137 | 1.6258 | 1.9646 | 2.3249 | 2.7008 | 3.085 | 3.4694 | 3.8447 | 4.2016 | 4.5302 | 4.821 | 5.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair line-to-line fault | Corrective | AC Wiring | 1 | 1 | 1 | N/A |  | Master electrician | 23.1971 | 25 | 1 | Weibull | 1 | 1 | 20 | 23.1971 | 20 | 43.1971 |  |  | 1.4072 | 15.5694 | 0.0113% | 1.6933 | 1.6595 | 1.6263 | 1.5938 | 1.5619 | 1.5307 | 1.5001 | 1.4701 | 1.4407 | 1.4119 | 1.3837 | 1.356 | 1.3289 | 1.3023 | 1.2763 | 1.2507 | 1.2257 | 1.2012 | 1.1772 | 1.1537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace broken/crushed AC wiring conduit and fittings | Corrective | AC wiring | 1 | 1 | 1 | N/A | strings | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 103.0445 | 0.25 | 10 | 371.5547 | 1030.445 | 1401.9996 |  |  | 45.6717 | 505.3188 | 0.3668% | 54.9587 | 53.8598 | 52.7829 | 51.7275 | 50.6932 | 49.6796 | 48.6863 | 47.7128 | 46.7588 | 45.8239 | 44.9076 | 44.0097 | 43.1298 | 42.2674 | 41.4223 | 40.594 | 39.7824 | 38.9869 | 38.2074 | 37.4434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate underground DC wiring | Corrective | DC wiring | 1 | 1 | 1 | N/A |  | Utilities locator | 18.5144 | 25 | 1 | Weibull | 1 | 2 | 0 | 37.0288 | 0 | 37.0288 |  |  | 1.2063 | 13.3462 | 0.009687% | 1.4515 | 1.4225 | 1.3941 | 1.3662 | 1.3389 | 1.3121 | 1.2859 | 1.2602 | 1.235 | 1.2103 | 1.1861 | 1.1624 | 1.1391 | 1.1163 | 1.094 | 1.0721 | 1.0507 | 1.0297 | 1.0091 | 0.98894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace broken/crushed DC wiring conduit and fittings | Corrective | DC wiring | 1 | 1 | 1 | N/A |  | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 1 | 4 | 100 | 57.6923 | 100 | 157.6923 |  |  | 5.137 | 56.8366 | 0.04125% | 6.1816 | 6.058 | 5.9368 | 5.8181 | 5.7018 | 5.5878 | 5.4761 | 5.3666 | 5.2593 | 5.1541 | 5.0511 | 4.9501 | 4.8511 | 4.7541 | 4.659 | 4.5659 | 4.4746 | 4.3851 | 4.2974 | 4.2115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace failed DC fuses in combiner box | Corrective | DC wiring | 1 | 1 | 1 | N/A | strings | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 103.0445 | 0.08 | 1 | 118.8975 | 103.0445 | 221.942 |  |  | 7.23 | 79.9939 | 0.05806% | 8.7002 | 8.5262 | 8.3557 | 8.1887 | 8.0249 | 7.8645 | 7.7072 | 7.5531 | 7.4021 | 7.2541 | 7.1091 | 6.9669 | 6.8276 | 6.6911 | 6.5573 | 6.4262 | 6.2977 | 6.1718 | 6.0484 | 5.9274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-route conduit | Corrective | DC wiring | 1 | 1 | 1 | N/A |  | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 1 | 4 | 100 | 57.6923 | 100 | 157.6923 |  |  | 5.137 | 56.8366 | 0.04125% | 6.1816 | 6.058 | 5.9368 | 5.8181 | 5.7018 | 5.5878 | 5.4761 | 5.3666 | 5.2593 | 5.1541 | 5.0511 | 4.9501 | 4.8511 | 4.7541 | 4.659 | 4.5659 | 4.4746 | 4.3851 | 4.2974 | 4.2115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RE-install inverter control software | Corrective | Inverter | 1 | 1 | 1 | EPC | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 0 | 24.0385 | 0 | 24.0385 |  |  | 0.37775 | 2.7427 | 0.001991% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86222 | 0.83657 | 0.81168 | 0.78754 | 0.76411 | 0.74139 | 0.71933 | 0.69793 | 0.67717 | 0.65703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace 24VDC power supply for inverter controls | Corrective | Inverter | 1 | 1 | 1 | EPC | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 120 | 24.0385 | 120 | 144.0385 |  |  | 2.2635 | 16.434 | 0.01193% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1664 | 5.0127 | 4.8636 | 4.7189 | 4.5786 | 4.4424 | 4.3102 | 4.182 | 4.0576 | 3.9369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace AC contactor in inverter | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 2 | 40 | 48.0769 | 40 | 88.0769 |  |  | 1.3841 | 10.0491 | 0.007294% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1592 | 3.0652 | 2.974 | 2.8855 | 2.7997 | 2.7164 | 2.6356 | 2.5572 | 2.4812 | 2.4074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace capacitors in inverter | Corrective | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 2 | 20000 | 48.0769 | 20000 | 20048.0769 |  |  | 316.0646 | 2301.968 | 1.671% | 2.3323 | 2.263 | 2.1956 | 2.1303 | 2.067 | 2.0055 | 1.9458 | 1.8879 | 1.8318 | 1.7773 | 719.089 | 697.699 | 676.9452 | 656.8088 | 637.2714 | 618.3151 | 599.9228 | 582.0775 | 564.763 | 547.9636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace DC contactor in inverter | Corrective | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 2 | 40 | 48.0769 | 40 | 88.0769 |  |  | 2.4059 | 24.6434 | 0.01789% | 2.3323 | 2.263 | 2.1956 | 2.1303 | 2.067 | 2.0055 | 1.9458 | 1.8879 | 1.8318 | 1.7773 | 3.1592 | 3.0652 | 2.974 | 2.8855 | 2.7997 | 2.7164 | 2.6356 | 2.5572 | 2.4812 | 2.4074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace fuses internal to inverter | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 0.25 | 25 | 6.0096 | 25 | 31.0096 |  |  | 0.4873 | 3.538 | 0.002568% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1123 | 1.0792 | 1.0471 | 1.0159 | 0.98571 | 0.95639 | 0.92794 | 0.90034 | 0.87355 | 0.84757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace GFI components in inveter | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 120 | 24.0385 | 120 | 144.0385 |  |  | 2.2635 | 16.434 | 0.01193% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1664 | 5.0127 | 4.8636 | 4.7189 | 4.5786 | 4.4424 | 4.3102 | 4.182 | 4.0576 | 3.9369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace IGBT driver card/board; diagnose with fault code | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 2 | 1000 | 48.0769 | 1000 | 1048.0769 |  |  | 16.4699 | 119.5797 | 0.08679% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.5927 | 36.4744 | 35.3895 | 34.3368 | 33.3154 | 32.3244 | 31.3629 | 30.4299 | 29.5248 | 28.6465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace IGBT matrix in inverter | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 4 | 80000 | 96.1538 | 80000 | 80096.1538 |  |  | 1258.6601 | 9138.5242 | 6.633% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2872.9072 | 2787.4497 | 2704.5343 | 2624.0852 | 2546.0292 | 2470.2951 | 2396.8137 | 2325.5181 | 2256.3433 | 2189.2261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inductors (coils) in inverter | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 4 | 20000 | 96.1538 | 20000 | 20096.1538 |  |  | 315.7983 | 2292.859 | 1.664% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720.8134 | 699.3721 | 678.5686 | 658.3839 | 638.7996 | 619.7979 | 601.3614 | 583.4733 | 566.1173 | 549.2776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter control card (PWM signal, voltage, phase, frequency, shut-down); diagnose with fault code | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 1000 | 24.0385 | 1000 | 1024.0385 |  |  | 16.0921 | 116.8371 | 0.0848% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.7304 | 35.6379 | 34.5778 | 33.5492 | 32.5513 | 31.583 | 30.6435 | 29.732 | 28.8476 | 27.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter data acquisition card/board (also called system input module); diagnose with fault code | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 1000 | 24.0385 | 1000 | 1024.0385 |  |  | 16.0921 | 116.8371 | 0.0848% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.7304 | 35.6379 | 34.5778 | 33.5492 | 32.5513 | 31.583 | 30.6435 | 29.732 | 28.8476 | 27.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter relay/switch | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 55 | 24.0385 | 55 | 79.0385 |  |  | 1.242 | 9.0178 | 0.006545% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.835 | 2.7506 | 2.6688 | 2.5894 | 2.5124 | 2.4377 | 2.3652 | 2.2948 | 2.2265 | 2.1603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace maximum power point tracker card/board; diagnose with fault code | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 1000 | 24.0385 | 1000 | 1024.0385 |  |  | 16.0921 | 116.8371 | 0.0848% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.7304 | 35.6379 | 34.5778 | 33.5492 | 32.5513 | 31.583 | 30.6435 | 29.732 | 28.8476 | 27.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace overvoltage surge suppressors for inverter | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 25 | 24.0385 | 25 | 49.0385 |  |  | 0.77061 | 5.595 | 0.004061% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7589 | 1.7066 | 1.6558 | 1.6066 | 1.5588 | 1.5124 | 1.4674 | 1.4238 | 1.3814 | 1.3403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace terminal block | Corrective | Inverter | 1 | 1 | 1 | Inverter | Combiner Box | Journeyman electrician | 14.4231 | 5 | 3 | Interval | 18 | 0.25 | 10 | 64.9038 | 180 | 244.9038 |  |  | 34.6761 | 213.5076 | 0.155% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.6083 | 0 | 0 | 0 | 0 | 363.9142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Restore lost internet connection | Corrective | Monitoring | 1 | 1 | 1 | N/A | Site | Network/IT | 33.25 | 20 | 3 | Interval | 1 | 1 | 0 | 33.25 | 0 | 33.25 |  |  | 2.4704 | 12.7679 | 0.009267% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Excavate and replace failed foundation element | Corrective | PV Array | 1 | 1 | 1 | N/A |  | Structural engineer | 40.4519 | 25 | 3 | Weibull | 103.0445 | 4 | 400 | 16673.3922 | 41217.7986 | 57891.1908 |  |  | 1648.3766 | 12353.7495 | 8.966% | 11.3367 | 46.233 | 105.9757 | 191.7147 | 304.3548 | 444.4404 | 612.0366 | 806.6109 | 1026.9229 | 1270.9269 | 1535.6987 | 1817.3927 | 2111.2389 | 2411.5881 | 2712.0094 | 3005.4446 | 3284.4178 | 3541.2963 | 3768.5937 | 3959.2996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace transformer | Corrective | Transformer | 1 | 0 | 0 | N/A | Transformer | Master electrician | 23.1971 | 50 | 2 | Weibull | 1 | 4 | 22000 | 92.7885 | 22000 | 22092.7885 |  |  | 223.9212 | 1846.9975 | 1.341% | 18.0205 | 36.7177 | 56.0659 | 76.0364 | 96.5981 | 117.7169 | 139.3566 | 161.4782 | 184.0405 | 207.0001 | 230.3113 | 253.9268 | 277.7972 | 301.8716 | 326.0978 | 350.4221 | 374.7899 | 399.1458 | 423.4335 | 447.5967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-tap transformer | Corrective | Transformer | 1 | 0 | 0 | N/A | Transformer | Master electrician | 23.1971 | 25 | 3 | Weibull | 1 | 2 | 0 | 46.3942 | 0 | 46.3942 |  |  | 1.321 | 9.9003 | 0.007186% | 0.0090853 | 0.037051 | 0.084929 | 0.15364 | 0.24391 | 0.35618 | 0.49049 | 0.64642 | 0.82298 | 1.0185 | 1.2307 | 1.4565 | 1.692 | 1.9327 | 2.1734 | 2.4086 | 2.6321 | 2.838 | 3.0202 | 3.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meet with key site staff to continue awareness, question any issues, and report on findings. | Administration | Documents | 1 | 0 | 0 | N/A |  | Administrator | 16.6635 | 1 | 1 | interval | 1 | 2 | 0 | 33.3269 | 0 | 33.3269 |  |  | 41.2976 | 418.8015 | 0.304% | 33.9935 | 34.6733 | 35.3668 | 36.0741 | 36.7956 | 37.5315 | 38.2822 | 39.0478 | 39.8288 | 40.6253 | 41.4378 | 42.2666 | 43.1119 | 43.9742 | 44.8537 | 45.7507 | 46.6657 | 47.5991 | 48.551 | 49.5221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bird Cleaning | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | acres | Cleaner | 10.6779 | 0.5 | 1 | interval | 1 | 4 | 120 | 42.7115 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Snow Removal | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | acres | Mower/Trimmer | 21.2308 | 0.5 | 1 | interval | 1 | 2 | 100 | 42.4615 | 100 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pollen Cleaning | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | acres | Cleaner | 10.6779 | 1 | 1 | interval | 1 | 4 | 120 | 42.7115 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dust Removal | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | acres | Cleaner | 10.6779 | 1 | 1 | interval | 1 | 4 | 120 | 42.7115 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Daily Operations and Performance Monitoring | Preventive | Asset Management | 0 | 0 | 0 | N/A |  | Administrator | 16.6635 | 0.083333 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monitor alarms and site-specific altert parameters | Preventive | Asset Management | 0 | 0 | 0 | N/A |  | Administrator | 16.6635 | 0.083333 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check Grounding Braids for wear | Preventive | Tracker | 0 | 0 | 0 | N/A | Structure | Inspector | 25.1731 | 1 | 1 | interval | 206.089 | 0.004 | 0 | 20.7516 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Anemometer inspection | Preventive | Tracker | 0 | 0 | 0 | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 1 | 0.1 | 0 | 2.5173 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Driveshaft torque check & visual inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | Driveshaft | Inspector | 25.1731 | 1 | 1 | interval | 0 | 0.0083333 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gearbox lubrication | Preventive | Tracker | 0 | 0 | 0 | N/A | block | Mechanic | 21.2308 | 0.5 | 1 | interval | 103.0445 | 0.25 | 0 | 546.9285 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inclinometer inspection | Preventive | Tracker | 0 | 0 | 0 | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 1 | 0.1 | 0 | 2.5173 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Limit switch inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | block | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical labor mobilization | Preventive | Mechanical | 0 | 0 | 0 | EPC | Site | Mechanic | 21.2308 | 1 | 1 | interval | 1 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Module table inpsection | Preventive | Tracker | 0 | 0 | 0 | N/A | connection | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Screw jack greasing | Preventive | Tracker | 0 | 0 | 0 | N/A | block | Mechanic | 21.2308 | 0.5 | 1 | interval | 103.0445 | 0.25 | 0 | 546.9285 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Screw jack inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | block | Inspector | 25.1731 | 0.5 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slew gear lubrication | Preventive | Tracker | 0 | 0 | 0 | N/A | Slew Gear | Mechanic | 21.2308 | 3 | 1 | interval | 0 | 0.25 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slew gear torque check & wear inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | Slew Gear | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.016667 | 0 | 43.2325 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Torque inspection | Preventive | Mechanical | 0 | 0 | 0 | N/A | block | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tracking Controller inspection | Preventive | Tracker | 0 | 0 | 0 | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Universal joint greasing (zirc fitting) | Preventive | Tracker | 0 | 0 | 0 | N/A | Driveshaft | Mechanic | 21.2308 | 0.5 | 1 | interval | 0 | 0.16667 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Universal joint inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | Driveshaft | Inspector | 25.1731 | 1 | 1 | interval | 0 | 0.0083333 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Spot-check monitoring instruments (pyranometer, etc) with hand-held instruments to ensure that they are operational and within specifications. | Preventive | Monitoring | 0 | 0 | 0 | N/A |  | Inspector | 25.1731 | 1 | 1 | interval | 1 | 1 | 0 | 25.1731 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect ballasted, non-penetrating mounting system for abnormal movement | Preventive | PV Array | 0 | 0 | 0 | N/A | rows | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.08 | 0 | 207.5158 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remove bird nests from array and rack area. | Preventive | PV Array | 0 | 0 | 0 | N/A | Acres | Pest control | 14.5865 | 1 | 1 | interval | 2.3153 | 4 | 0 | 135.0876 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walk through each row of the PV array and check the PV modules for any damage. Report any damage to rack and damaged modules for warranty replacement. Note location and serial number of questionable modules. | Preventive | PV Array | 1 | 0 | 0 | N/A | Acres | Inspector | 25.1731 | 1 | 1 | interval | 2.3153 | 0.5 | 0 | 29.1413 | 0 | 29.1413 |  |  | 36.111 | 366.2035 | 0.2658% | 29.7242 | 30.3187 | 30.925 | 31.5435 | 32.1744 | 32.8179 | 33.4742 | 34.1437 | 34.8266 | 35.5231 | 36.2336 | 36.9583 | 37.6974 | 38.4514 | 39.2204 | 40.0048 | 40.8049 | 41.621 | 42.4534 | 43.3025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lubricate tracker mounting bearings/gimbals | Preventive | Tracker | 0 | 0 | 0 | N/A |  | Mechanic | 21.2308 | 1 | 1 | interval | 103.0445 | 0.15 | 1 | 328.1571 | 103.0445 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect transformer meter, oil and tempertaure gauges | Preventive | Transformer | 0 | 0 | 0 | N/A |  | Master electrician | 23.1971 | 1 | 1 | interval | 1 | 0.25 | 0 | 5.7993 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracking controller power supply fan filter | Corrective | Tracker | 0 | 1 | 1 | EPC | Controller | Mechanic | 21.2308 | 2 | 1 | interval | 103.0445 | 0.16667 | 25 | 364.619 | 2576.1124 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair roof leaks | Corrective | Roof | 0 | 1 | 1 | N/A | acres | Roofing | 16.4519 | 25 | 1 | Weibull | 2.3153 | 8 | 400 | 304.7263 | 926.1115 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-roof (new roof) | Corrective | Roof | 0 | 1 | 1 | N/A | acres | Roofing | 16.4519 | 30 | 4 | Weibull | 2.3153 | 24 | 75000 | 914.1789 | 173645.9016 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair/replace tracker drive shaft | Corrective | Tracker | 0 | 1 | 1 | N/A | row | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 0.5 | 120 | 1093.857 | 12365.3396 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace hydraulic cylinder | Corrective | Tracker | 0 | 1 | 1 | N/A |  | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 0.5 | 120 | 1093.857 | 12365.3396 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracker drive bearing | Corrective | Tracker | 0 | 1 | 1 | N/A | row | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 0.5 | 40 | 1093.857 | 4121.7799 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracker motor controller | Corrective | Tracker | 0 | 1 | 1 | N/A |  | Journeyman electrician | 14.4231 | 25 | 3 | Weibull | 103.0445 | 0.5 | 250 | 743.1093 | 25761.1241 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracker mount bearing | Corrective | Tracker | 0 | 1 | 1 | N/A |  | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 0.5 | 40 | 1093.857 | 4121.7799 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace/upgrade tracker control software | Corrective | Tracker | 0 | 1 | 1 | N/A |  | Network/IT | 33.25 | 25 | 3 | Weibull | 103.0445 | 1 | 0 | 3426.2295 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manage inventory of spare parts | Administration | Asset Management | 1 | 1 | 1 | Monitoring |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 16.6635 |  |  | 202.8276 | 1713.259 | 1.243% | 0 | 0 | 0 | 0 | 0 | 234.5721 | 239.2635 | 244.0488 | 248.9297 | 253.9083 | 258.9865 | 264.1662 | 269.4496 | 274.8385 | 280.3353 | 285.942 | 291.6609 | 297.4941 | 303.444 | 309.5128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Confirm availability and take any measures to secure operating instructions, warranties and performance guarantees, and other project documentation. | Administration | Documents | 1 | 0 | 0 | N/A |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 16.6635 |  |  | 258.1099 | 2617.5091 | 1.9% | 212.4591 | 216.7083 | 221.0425 | 225.4633 | 229.9726 | 234.5721 | 239.2635 | 244.0488 | 248.9297 | 253.9083 | 258.9865 | 264.1662 | 269.4496 | 274.8385 | 280.3353 | 285.942 | 291.6609 | 297.4941 | 303.444 | 309.5128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Document all O&M activities in a workbook available to all service personnel. | Administration | Documents | 0 | 0 | 0 | N/A |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Review O&M agreements and ensure that services are actually provided | Administration | Documents | 1 | 0 | 0 | N/A |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 16.6635 |  |  | 258.1099 | 2617.5091 | 1.9% | 212.4591 | 216.7083 | 221.0425 | 225.4633 | 229.9726 | 234.5721 | 239.2635 | 244.0488 | 248.9297 | 253.9083 | 258.9865 | 264.1662 | 269.4496 | 274.8385 | 280.3353 | 285.942 | 291.6609 | 297.4941 | 303.444 | 309.5128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Update record with preventative maintenance activities and track any problems or warranty issues and secure the record on-site. | Administration | Documents | 1 | 0 | 0 | N/A |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 16.6635 |  |  | 258.1099 | 2617.5091 | 1.9% | 212.4591 | 216.7083 | 221.0425 | 225.4633 | 229.9726 | 234.5721 | 239.2635 | 244.0488 | 248.9297 | 253.9083 | 258.9865 | 264.1662 | 269.4496 | 274.8385 | 280.3353 | 285.942 | 291.6609 | 297.4941 | 303.444 | 309.5128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maintain a log of cumulative power delivery (kWh to date) and chart this value against date. Chart the value even for uneven or infrequent intervals. Explain variation by season or weather. | Administration | Meter | 0 | 0 | 0 | N/A |  | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 0.5 | 0 | 8.3317 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 16682.456 | 137778.286 | 100% | 4404.1281 | 4541.8165 | 4706.8062 | 4900.2543 | 10709.2686 | 5689.952 | 5978.9451 | 6297.5071 | 6644.3934 | 13185.1653 | 21998.5371 | 22564.235 | 23187.7428 | 23858.9051 | 32410.9667 | 25298.5787 | 26042.4737 | 26785.4254 | 27514.858 | 36929.1611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Labor Rates
Service Category | Rate $/hour | Scope of Work | Salary (2080 hrs/year) | Qualifications
Administrator | 16.6635 | Record-keeping, service confirmation, correspondence | 34660 | Excellent interpersonal and communication skills (written and verbal). Diligent record keeping. 2 to 5 years of experience. Excellent MS Office and computer skills. Management of contractors and quality.
Cleaner | 10.6779 | Cleaning PV Arrays | 22210 | 10 OSHA Card; Required level of bonding and insurance; drivers license and reliable transportation; minimum 18 years old.
Designer | 42.2692 | Specifications, drawings, modeling and analysis, codes and standards. | 87920 | B.S. in EE (4-year engineering degree); registered PE licensed to practice engineering in the jurisdiction; NABCEP PV Installer Certification; CAD (AutoCAD) and graphics skills; knowledge of IEEE, NEC, NESC, and other codes and standards for PV systems; required level of errors and omissions insurance.
Inspector | 25.1731 | Diagnostic analysis; visual inspection, specific testing, | 52360 | Diagnostic analysis; NABCEP PV Installer Certification; 2 to 5 years of experience.
Inverter specialist | 24.0385 | Inverter repair, upgrades | 50000 | (estimated) Skills to perform maintenance, diagnostics and repair for inverter: factory trained and certified; 5+ years experience.
Journeyman electrician | 14.4231 | Module replacement, Inverter replacement, fuse/breaker replacement, conduit routing, wiring, ground fault repair | 30000 | (estimated) 50 OSHA Card; training in arc-flash, lock-out/tag-out, and other special protective equipment and procedures; NABCEP PV Installer certification; experience in the design of medium voltage electrical systems. 5+ years experience with PV systems; color vision.
Master electrician | 23.1971 | Module replacement, inverter replacement, fuse/breaker replacement, conduit routing, wiring, ground fault repair | 48250 | Electrical Contractor’s license for the jurisdictions; 50 OSHA Card; NABCEP PV Installer certification; experience in the design of medium voltage electrical systems. 5+ years experience with PV systems; color vision. Certification by the North American Energy Reliability Corporation (NERC) is necessary for positions that affect the power grid.
Mechanic | 21.2308 | Maintenance and repair/replace of tracking mount components | 44160 | 50 OSHA Card; 2 to 5 years of experience; required level of bonding and insurance.
Network/IT | 33.25 | Internet/network repair, monitoring equipment repair | 69160 | Knowledge of specific monitoring devices (training by system supplier) and how monitoring system is connected through network connections or wireless or cellular modem; knowledge of Modbus, DNP3 and other protocols, HMI operator interfaces; 2 to 5 years of experience. Locus, Enphase, Itron, etc. monitoring device knowledge.
Pest control | 14.5865 | Nesting vermin removal, Nesting vermin prevention | 30340 | 10 OSHA Card; safety training in handling animals and detritus; required level of bonding and insurance; drivers license and reliable transportation; minimum 18 years old; most states require license for pesticide
PV module/array Specialist | 24.0385 | Module repair | 50000 | (estimated) Skills to operate, troubleshoot, maintain, and repair photovoltaic equipment: NABCEP PV Installer certification. 2 to 5 years of experience.
Roofing | 16.4519 | Roof leak repair, roof tile repair, re-roof | 34220 | Roofing contractor’s license for the jurisdiction; 10 OSHA Card; safety training in fall protection equipment and use (or 50 OSHA Card); required level of bonding and insurance
Structural engineer | 40.4519 | Foundations and rack inspection/design | 84140 | B.S. CE (4-year engineering degree); registered PE licensed to practice engineering in the jurisdiction.
Mower/Trimmer | 11.4135 | Removal of vegetation | 23740 | 50 OSHA Card; drivers license and reliable transportation; required level of insurance; minimum 18 years old; any required training or license for herbicide application.
Utilities locator | 18.5144 | Locate underground utilities. | 38510 | 2 to5 years of experience.

## Lists
PV System Alternatives
Category | PV Component | PV Module Type | Module Encapsulant | Mounting Structure Type | PV Sector | Environmental Conditions | Failure Distributions | Inverter Types
Administration | AC Wiring | Amorphous silicon:0.87%/year | Ethyl Vinyl Acetate (EVA) | Residential Rooftop (<= 10kW) | All | Snow | Interval | String Inverter
Design | DC Wiring | Mono-crystal silicon: 0.36%/year | Polyvinyl Butyral (PVB) | Commercial Rooftop (10kW - 1000kW) | Residential (10 kW) | Humid | Weibull | Central Inverter
Preventive | Documents | Mulit-crystal Silicon:0.64%/year | Silicone | Grount-Mount Fixed Tilt (> 100kW) | Commercial (1000 kW) | Hot (reduce efficiency 2.67% for central, 0.18% for string inverter, Wang et al 2012) |  | Microinverter (not yet implemented, do not use)
Corrective | Inverter | Cadmium telluride: 0.40%/year |  | Ground-Mount Tracker (> 100kW) | Utility (1 MW) | Pollen
Decommission | Meter | CIGS:0.96%/year |  |  |  | High Wind
| Monitoring System | Concentrator |  |  |  | Hail
| PV Array |  |  |  |  | Salt Air
| PV Modules |  |  |  |  | Diesel Soot (reduce efficiency 1%/g, Wang et al 2012)
| Tracking Mechanism |  |  |  |  | Industrial Emissions (reduce efficiency 1%/g, Wang et al 2012)
| Rack |  |  |  |  | Bird Populations
| Roof |  |  |  |  | Construction Site Nearby (reduce efficiency 1%/g, Wang et al 2012)
| Transformer |  |  |  |  | Sand/Dust (reduce efficiency 1%/g, Wang et al 2012)
| Cleaning/Veg |  |  |  |  | High Insolation (reduce availability 0.83%, Wang et al 2012)
[9 empty] | Warranty Types | Years
Service Category | Scope of Work | Salary(2080 hrs/year) | Qualifications | [5 empty] | EPC | 10
Administrator | Record-keeping, service confirmation, correspondence | 34660 | Excellent interpersonal and communication skills (written and verbal). Diligent record keeping. 2 to 5 years of experience. Excellent MS Office and computer skills. | [5 empty] | Inverter | 10
Designer | Specifications, drawings, modeling and analysis, codes and standards. | 87920 | B.S. in EE (4-year engineering degree); registered PE licensed to practice engineering in the jurisdiction; NABCEP PV Installer Certification; CAD (AutoCAD) and graphics skills; knowledge of IEEE, NEC, NESC, and other codes and standards for PV systems; required level of errors and omissions insurance. | [5 empty] | Module (Product) | 10
Cleaner | Cleaning PV Arrays | 22210 | 10 OSHA Card; Required level of bonding and insurance; drivers license and reliable transportation; minimum 18 years old. | [5 empty] | Monitoring | 5
Tree trimmer | Removal of vegetation | 23740 | 50 OSHA Card; drivers license and reliable transportation; required level of insurance; minimum 18 years old; any required training or license for herbicide application. | [5 empty] | N/A | 0
Pest control | Nesting vermin removal, Nesting vermin prevention | 30340 | 10 OSHA Card; safety training in handling animals and detritus; required level of bonding and insurance; drivers license and reliable transportation; minimum 18 years old; most states require license for pesticide
Roofing | Roof leak repair, roof tile repair, re-roof | 34220 | Roofing contractor’s license for the jurisdiction; 10 OSHA Card; safety training in fall protection equipment and use (or 50 OSHA Card); required level of bonding and insurance
2 to 5 years of experience.
Structural engineer | Foundations and rack inspection/design | 84140 | B.S. CE (4-year engineering degree); registered PE licensed to practice engineering in the jurisdiction.
Mechanic | Maintenance and repair/replace of tracking mount components | 44160 | 50 OSHA Card; 2 to 5 years of experience; required level of bonding and insurance.
Master electrician | Module replacement, inverter replacement, fuse/breaker replacement, conduit routing, wiring, ground fault repair | 48250 | Electrical Contractor’s license for the jurisdictions; 50 OSHA Card; NABCEP PV Installer certification; experience in the design of medium voltage electrical systems. 5+ years experience with PV systems; color vision. Certification by the North American Energy Reliability Corporation (NERC) is necessary for positions that affect the power grid.
Journeyman electrician | Module replacement, Inverter replacement, fuse/breaker replacement, conduit routing, wiring, ground fault repair | $30,000 (estimated) | 50 OSHA Card; training in arc-flash, lock-out/tag-out, and other special protective equipment and procedures; NABCEP PV Installer certification; experience in the design of medium voltage electrical systems. 5+ years experience with PV systems; color vision.
Network/IT | Internet/network repair, monitoring equipment repair | 69160 | Knowledge of specific monitoring devices (training by system supplier) and how monitoring system is connected through network connections or wireless or cellular modem; knowledge of Modbus, DNP3 and other protocols, HMI operator interfaces; 2 to 5 years of experience. Locus, Enphase, Itron, etc. monitoring device knowledge.
Inspection | Diagnostic analysis; visual inspection, specific testing, | 52360 | Diagnostic analysis; NABCEP PV Installer Certification; 2 to 5 years of experience.
Inverter specialist | Inverter repair, upgrades | $50,000 (estimated) | Skills to perform maintenance, diagnostics and repair for inverter: factory trained and certified; 5+ years experience.
PV module/array Specialist | Module repair | $50,000 (estimated) | Skills to operate, troubleshoot, maintain, and repair photovoltaic equipment: NABCEP PV Installer certification. 2 to 5 years of experience.
Utilities locator | Locate underground utilities. | 38510 | 2 to5 years of experience.

## Reports
Lifetime NPV by Service Type
Service | Avg. Cost/Yr | NPV (Life) | % of Total
Designer | 0 | 0 | 0%
Pest control | 146.1662 | 1482.2804 | 1.076%
Roofing | 0 | 0 | 0%
Structural engineer | 1648.3766 | 12353.7495 | 8.966%
Mower/Trimmer | 741.2247 | 7516.8074 | 5.456%
Utilities locator | 3.315 | 29.1498 | 0.02116%
Mechanic | 871.9334 | 5840.0329 | 4.239%
Master electrician | 432.2165 | 3658.5181 | 2.655%
Network/IT | 145.9282 | 1294.445 | 0.9395%
PV module/array Specialist | 1257.5467 | 10753.8019 | 7.805%
Journeyman electrician | 4258.2291 | 31674.1499 | 22.99%
Inspector | 1763.2589 | 17874.0771 | 12.97%
Inverter specialist | 3271.3815 | 24030.4039 | 17.44%
Cleaner | 807.8295 | 8192.2507 | 5.946%
Administrator | 1335.0497 | 13078.6194 | 9.493%
Total | 16682.456 | 137778.286 | 100%
Lifetime NPV by Component Type
Component | Avg. Cost/Yr | NPV (Life) | % of Total
Monitoring | 2.4704 | 12.7679 | 0.009394%
Inverter | 3302.2265 | 24461.5826 | 18%
AC Wiring | 153.2395 | 1590.761 | 1.17%
Mechanical | 733.5631 | 7321.1813 | 5.386%
DC Wiring | 1735.4148 | 14725.0595 | 10.83%
PV Module | 4531.6551 | 34244.4307 | 25.19%
Meter | 0 | 0 | 0%
Electrical | 416.7669 | 3660.6886 | 2.693%
PV Array | 2967.0034 | 23813.4279 | 17.52%
Cleaning/Veg | 1547.7311 | 15695.6397 | 11.55%
Asset Management | 251.5156 | 2124.5203 | 1.563%
Documents | 815.6273 | 8271.3287 | 6.085%
Total | 16457.2138 | 135921.3882 | 100%
Lifetime NPV by Activity
Component | Avg. Cost/Yr | NPV (Life) | % of Total
Administrative | 0 | 0 | 0%
Preventive | 5829.9755 | 56999.8233 | 41.94%
Corrective | 9834.0255 | 70793.8749 | 52.08%
Total | 15664.0011 | 127793.6982 | 94.02%

## Cash Flow
Activity Description | Activity Type | Component Type | Applicable ? (1= yes, 0 = no) | Covered by Warranty? (1=yes, 0=no) | Covered by Warranty? (1=yes, 0=no) | Warranty Type | Applicable Unit | Service Category | Labor Rate per Hour | Mean Interval (years) | Weibull or Lognormal Shape Factor | Type of Distribution | Approx. Number of Units | Labor hrs per unit | Material/ Other Cost per unit | Total Labor Cost | Total Matl and Other Cost | Total Cost for Measure | Notes | Reference | Average Annual Expense | NPV (Project Life) | % of Total NPV | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
Manage inventory of spare parts | Administration | Asset Management | 1 | 1 | 1 | Monitoring | 0 | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 16.6635 | 0 | 0 | 202.8276 | 1713.259 | 1.243% | 0 | 0 | 0 | 0 | 0 | 234.5721 | 239.2635 | 244.0488 | 248.9297 | 253.9083 | 258.9865 | 264.1662 | 269.4496 | 274.8385 | 280.3353 | 285.942 | 291.6609 | 297.4941 | 303.444 | 309.5128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monitoring annual service package | Preventive | Asset Management | 1 | 1 | 1 | Monitoring | System | Administrator | 0 | 1 | 1 | interval | 1 | 0 | 50 | 0 | 50 | 50 | 0 | 0 | 48.688 | 411.2613 | 0.2985% | 0 | 0 | 0 | 0 | 0 | 56.3081 | 57.4343 | 58.583 | 59.7546 | 60.9497 | 62.1687 | 63.4121 | 64.6803 | 65.9739 | 67.2934 | 68.6393 | 70.0121 | 71.4123 | 72.8406 | 74.2974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Confirm availability and take any measures to secure operating instructions, warranties and performance guarantees, and other project documentation. | Administration | Documents | 1 | 0 | 0 | N/A | 0 | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 16.6635 | 0 | 0 | 258.1099 | 2617.5091 | 1.9% | 212.4591 | 216.7083 | 221.0425 | 225.4633 | 229.9726 | 234.5721 | 239.2635 | 244.0488 | 248.9297 | 253.9083 | 258.9865 | 264.1662 | 269.4496 | 274.8385 | 280.3353 | 285.942 | 291.6609 | 297.4941 | 303.444 | 309.5128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Document all O&M activities in a workbook available to all service personnel. | Administration | Documents | 0 | 0 | 0 | N/A | 0 | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Review O&M agreements and ensure that services are actually provided | Administration | Documents | 1 | 0 | 0 | N/A | 0 | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 16.6635 | 0 | 0 | 258.1099 | 2617.5091 | 1.9% | 212.4591 | 216.7083 | 221.0425 | 225.4633 | 229.9726 | 234.5721 | 239.2635 | 244.0488 | 248.9297 | 253.9083 | 258.9865 | 264.1662 | 269.4496 | 274.8385 | 280.3353 | 285.942 | 291.6609 | 297.4941 | 303.444 | 309.5128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Update record with preventative maintenance activities and track any problems or warranty issues and secure the record on-site. | Administration | Documents | 1 | 0 | 0 | N/A | 0 | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 16.6635 | 0 | 0 | 258.1099 | 2617.5091 | 1.9% | 212.4591 | 216.7083 | 221.0425 | 225.4633 | 229.9726 | 234.5721 | 239.2635 | 244.0488 | 248.9297 | 253.9083 | 258.9865 | 264.1662 | 269.4496 | 274.8385 | 280.3353 | 285.942 | 291.6609 | 297.4941 | 303.444 | 309.5128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maintain a log of cumulative power delivery (kWh to date) and chart this value against date. Chart the value even for uneven or infrequent intervals. Explain variation by season or weather. | Administration | Meter | 0 | 0 | 0 | N/A | 0 | Administrator | 16.6635 | 0.08 | 1 | interval | 1 | 0.5 | 0 | 8.3317 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace protective devices (breakers) in building panel | Corrective | AC wiring | 1 | 1 | 1 | N/A | 0 | Master electrician | 23.1971 | 25 | 1 | Weibull | 3 | 0.25 | 10 | 17.3978 | 30 | 47.3978 | 0 | 0 | 1.544 | 17.0835 | 0.0124% | 1.858 | 1.8209 | 1.7844 | 1.7488 | 1.7138 | 1.6795 | 1.646 | 1.613 | 1.5808 | 1.5492 | 1.5182 | 1.4879 | 1.4581 | 1.4289 | 1.4004 | 1.3724 | 1.3449 | 1.318 | 1.2917 | 1.2659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter AC fuse(s) | Corrective | AC wiring | 1 | 1 | 1 | EPC | 0 | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 3 | 0.15 | 10 | 6.4904 | 30 | 36.4904 | 0 | 0 | 0.53454 | 3.8598 | 0.002801% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1688 | 1.1455 | 1.1226 | 1.1001 | 1.0781 | 1.0566 | 1.0354 | 1.0147 | 0.99444 | 0.97455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter | Corrective | Inverter | 1 | 1 | 1 | Inverter | Inverter | Inverter specialist | 24.0385 | 10 | 1 | Weibull | 1 | 0 | 80300 | 0 | 80300 | 80300 | $300 flat fee | 0 | 1189.3017 | 8869.1204 | 6.437% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3323.4833 | 3067.3563 | 2830.9679 | 2612.797 | 2411.4397 | 2225.6001 | 2054.0823 | 1895.7828 | 1749.6827 | 1614.8419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace MC connector lead to combiner box | Corrective | DC wiring | 1 | 1 | 1 | Module (Product) | modules | PV module/array Specialist | 24.0385 | 25 | 1 | Weibull | 1443 | 0.1 | 20 | 3468.75 | 28860 | 32328.75 | 0 | 0 | 473.5758 | 3419.6325 | 2.482% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1035.5265 | 1014.8214 | 994.5303 | 974.6449 | 955.1571 | 936.0589 | 917.3426 | 899.0006 | 881.0253 | 863.4094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seal Leaking Junction Box | Corrective | DC Wiring | 1 | 1 | 1 | Module (Product) | modules | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 1443 | 0.25 | 10 | 5203.125 | 14430 | 19633.125 | 0 | 0 | 287.6008 | 2076.7296 | 1.507% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 628.8712 | 616.2971 | 603.9744 | 591.8981 | 580.0632 | 568.465 | 557.0986 | 545.9596 | 535.0432 | 524.3452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace MC Connectors between modules | Corrective | DC wiring | 1 | 1 | 1 | Module (Product) | modules | PV module/array Specialist | 24.0385 | 25 | 1 | Weibull | 1443 | 0.1 | 5 | 3468.75 | 7215 | 10683.75 | 0 | 0 | 156.5036 | 1130.0931 | 0.8202% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342.2126 | 335.3702 | 328.6645 | 322.0929 | 315.6528 | 309.3414 | 303.1561 | 297.0946 | 291.1543 | 285.3327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate ground fault | Corrective | DC Wiring | 1 | 1 | 1 | EPC | 0 | Master electrician | 23.1971 | 25 | 1 | Weibull | 1 | 4 | 0 | 92.7885 | 0 | 92.7885 | 0 | 0 | 1.3592 | 9.8149 | 0.007124% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9721 | 2.9127 | 2.8545 | 2.7974 | 2.7414 | 2.6866 | 2.6329 | 2.5803 | 2.5287 | 2.4781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair ground fault | Corrective | DC Wiring | 1 | 1 | 1 | EPC | 0 | Master electrician | 23.1971 | 25 | 1 | Weibull | 1 | 1 | 20 | 23.1971 | 20 | 43.1971 | 0 | 0 | 0.63278 | 4.5693 | 0.003316% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3837 | 1.356 | 1.3289 | 1.3023 | 1.2763 | 1.2507 | 1.2257 | 1.2012 | 1.1772 | 1.1537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace fuse(s) on DC source circuits to inverter | Corrective | DC wiring | 1 | 1 | 1 | EPC | 0 | Master electrician | 23.1971 | 25 | 1 | Weibull | 18 | 0.08 | 5 | 33.4038 | 90 | 123.4038 | 0 | 0 | 1.8077 | 13.0533 | 0.009474% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9528 | 3.8737 | 3.7963 | 3.7204 | 3.646 | 3.5731 | 3.5016 | 3.4316 | 3.363 | 3.2958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Start/stop inverter (reboot to clear unknown error) | Corrective | Inverter | 1 | 0 | 0 | EPC | inverter | Inspector | 25.1731 | 1 | 3 | Interval | 1 | 0.25 | 0 | 6.2933 | 0 | 6.2933 | 0 | 0 | 7.7984 | 79.0841 | 0.0574% | 6.4191 | 6.5475 | 6.6785 | 6.812 | 6.9483 | 7.0872 | 7.229 | 7.3736 | 7.521 | 7.6715 | 7.8249 | 7.9814 | 8.141 | 8.3038 | 8.4699 | 8.6393 | 8.8121 | 8.9883 | 9.1681 | 9.3515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter fan motor | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 15 | 1 | Weibull | 1 | 1 | 120 | 24.0385 | 120 | 144.0385 | 0 | 0 | 2.3432 | 17.1677 | 0.01246% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7346 | 5.4721 | 5.2216 | 4.9825 | 4.7544 | 4.5367 | 4.329 | 4.1308 | 3.9417 | 3.7612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
manual reset of arc-fault trip (NEC 690.11) | Corrective | Inverter | 1 | 1 | 1 | EPC | inverter | Inverter specialist | 24.0385 | 25 | 1 | Weibull | 1 | 0.08 | 0 | 1.9231 | 0 | 1.9231 | 0 | 0 | 0.028171 | 0.20342 | 0.0001476% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061598 | 0.060367 | 0.05916 | 0.057977 | 0.056818 | 0.055682 | 0.054568 | 0.053477 | 0.052408 | 0.05136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dispatch contractor in response to alarms, alerts, or contact by others | Corrective | PV Array | 1 | 1 | 1 | Monitoring | 0 | Administrator | 16.6635 | 1 | 1 | Interval | 1 | 1 | 4 | 16.6635 | 4 | 20.6635 | 0 | 0 | 20.1212 | 169.9616 | 0.1234% | 0 | 0 | 0 | 0 | 0 | 23.2704 | 23.7358 | 24.2105 | 24.6947 | 25.1886 | 25.6924 | 26.2063 | 26.7304 | 27.265 | 27.8103 | 28.3665 | 28.9338 | 29.5125 | 30.1028 | 30.7048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair or replace rack parts damaged by corrosion or physical damage | Corrective | PV Array | 1 | 1 | 1 | EPC | 0 | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 1 | 200 | 2187.7139 | 20608.8993 | 22796.6132 | 0 | 0 | 554.1912 | 3741.5775 | 2.716% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604.7333 | 715.6598 | 831.3717 | 949.6443 | 1067.9454 | 1183.4954 | 1293.3505 | 1394.5051 | 1484.0112 | 1559.108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace modules failing performance test or IR scan | Corrective | PV module | 1 | 1 | 1 | Module (Product) | modules | Journeyman electrician | 14.4231 | 50 | 2 | Weibull | 1443 | 0.15 | 244 | 3121.875 | 352092 | 355213.875 | 0 | 0 | 2721.5633 | 18665.2308 | 13.55% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3703.0078 | 4082.7036 | 4466.4984 | 4853.5741 | 5243.0891 | 5634.1822 | 6025.9748 | 6417.5748 | 6808.08 | 7196.5811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair or replace damage to module frame | Corrective | PV module | 1 | 1 | 1 | Module (Product) | modules | Mechanic | 21.2308 | 50 | 3 | Weibull | 1443 | 0.25 | 50 | 7659 | 72150 | 79809 | 0 | 0 | 317.7421 | 2098.4555 | 1.523% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285.1189 | 345.0039 | 411.4517 | 484.6051 | 564.5758 | 651.4407 | 745.2369 | 845.9579 | 953.5489 | 1067.9027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair cracking of PV module back sheet | Corrective | PV module | 1 | 1 | 1 | Module (Product) | modules | Journeyman electrician | 14.4231 | 50 | 3 | Weibull | 1443 | 0.1 | 25 | 2081.25 | 36075 | 38156.25 | 0 | 0 | 151.9108 | 1003.2602 | 0.7282% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136.3138 | 164.9445 | 196.7128 | 231.6871 | 269.9206 | 311.4502 | 356.2937 | 404.4479 | 455.8866 | 510.5585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-torque all electrical connections on AC side of system. | Preventive | AC Wiring | 1 | 0 | 0 | N/A | 0 | Journeyman electrician | 14.4231 | 1 | 1 | interval | 1 | 0.5 | 0 | 7.2115 | 0 | 7.2115 | 0 | 0 | 8.9363 | 90.6235 | 0.06577% | 7.3558 | 7.5029 | 7.6529 | 7.806 | 7.9621 | 8.1214 | 8.2838 | 8.4495 | 8.6185 | 8.7908 | 8.9666 | 9.146 | 9.3289 | 9.5155 | 9.7058 | 9.8999 | 10.0979 | 10.2999 | 10.5058 | 10.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exercise operation of all protection devices. | Preventive | AC Wiring | 1 | 0 | 0 | N/A | 0 | Journeyman electrician | 14.4231 | 1 | 1 | interval | 2 | 0.08 | 0 | 2.3077 | 0 | 2.3077 | 0 | 0 | 2.8596 | 28.9995 | 0.02105% | 2.3538 | 2.4009 | 2.4489 | 2.4979 | 2.5479 | 2.5988 | 2.6508 | 2.7038 | 2.7579 | 2.8131 | 2.8693 | 2.9267 | 2.9852 | 3.045 | 3.1059 | 3.168 | 3.2313 | 3.296 | 3.3619 | 3.4291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check position of disconnect switches and breakers. | Preventive | AC Wiring | 1 | 0 | 0 | N/A | Disconnect Box | Inspector | 25.1731 | 1 | 1 | interval | 18 | 0.08 | 0 | 36.2492 | 0 | 36.2492 | 0 | 0 | 44.9188 | 455.5245 | 0.3306% | 36.9742 | 37.7137 | 38.468 | 39.2373 | 40.0221 | 40.8225 | 41.639 | 42.4718 | 43.3212 | 44.1876 | 45.0714 | 45.9728 | 46.8922 | 47.8301 | 48.7867 | 49.7624 | 50.7577 | 51.7728 | 52.8083 | 53.8645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect electrical boxes for corrosion or intrusion of water or insects. Seal boxes if required. | Preventive | AC Wiring | 1 | 0 | 0 | N/A | Combiner Box | Inspector | 25.1731 | 1 | 1 | interval | 18 | 0.08 | 0 | 36.2492 | 0 | 36.2492 | 0 | 0 | 44.9188 | 455.5245 | 0.3306% | 36.9742 | 37.7137 | 38.468 | 39.2373 | 40.0221 | 40.8225 | 41.639 | 42.4718 | 43.3212 | 44.1876 | 45.0714 | 45.9728 | 46.8922 | 47.8301 | 48.7867 | 49.7624 | 50.7577 | 51.7728 | 52.8083 | 53.8645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Daily Operations and Performance Monitoring | Preventive | Asset Management | 0 | 0 | 0 | N/A | 0 | Administrator | 16.6635 | 0.083333 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monitor alarms and site-specific altert parameters | Preventive | Asset Management | 0 | 0 | 0 | N/A | 0 | Administrator | 16.6635 | 0.083333 | 1 | interval | 1 | 1 | 0 | 16.6635 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bird Cleaning | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | acres | Cleaner | 10.6779 | 0.5 | 1 | interval | 1 | 4 | 120 | 42.7115 | 120 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pollen Cleaning | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | acres | Cleaner | 10.6779 | 1 | 1 | interval | 1 | 4 | 120 | 42.7115 | 120 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dust Removal | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | acres | Cleaner | 10.6779 | 1 | 1 | interval | 1 | 4 | 120 | 42.7115 | 120 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect cabling for signs of cracks, defects, pulling out of connections; overheating, arcing, short or open circuits, ground faults in wiring and condition of wire insulation and protective materials.. | Preventive | DC Wiring | 1 | 0 | 0 | N/A | strings | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 259.3947 | 0 | 0 | 321.4331 | 3259.6732 | 2.366% | 264.5826 | 269.8742 | 275.2717 | 280.7772 | 286.3927 | 292.1206 | 297.963 | 303.9222 | 310.0007 | 316.2007 | 322.5247 | 328.9752 | 335.5547 | 342.2658 | 349.1111 | 356.0933 | 363.2152 | 370.4795 | 377.8891 | 385.4469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check proper position of DC disconnect switches. | Preventive | DC Wiring | 1 | 0 | 0 | N/A | 0 | Inspector | 25.1731 | 1 | 1 | interval | 18 | 0.08 | 0 | 36.2492 | 0 | 36.2492 | 0 | 0 | 44.9188 | 455.5245 | 0.3306% | 36.9742 | 37.7137 | 38.468 | 39.2373 | 40.0221 | 40.8225 | 41.639 | 42.4718 | 43.3212 | 44.1876 | 45.0714 | 45.9728 | 46.8922 | 47.8301 | 48.7867 | 49.7624 | 50.7577 | 51.7728 | 52.8083 | 53.8645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Install software updates, inverter and other | Preventive | Electrical | 1 | 1 | 1 | EPC | NCU | Inverter specialist | 24.0385 | 5 | 1 | interval | 1 | 1 | 500 | 24.0385 | 500 | 524.0385 | 0 | 0 | 74.199 | 456.8576 | 0.3316% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705.2868 | 0 | 0 | 0 | 0 | 778.6936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter inspection | Preventive | Electrical | 1 | 0 | 0 | N/A | Inverter | Inspector | 25.1731 | 1 | 1 | interval | 1 | 1 | 0 | 25.1731 | 0 | 25.1731 | 0 | 0 | 31.1936 | 316.3365 | 0.2296% | 25.6765 | 26.1901 | 26.7139 | 27.2481 | 27.7931 | 28.349 | 28.916 | 29.4943 | 30.0842 | 30.6858 | 31.2996 | 31.9255 | 32.5641 | 33.2153 | 33.8796 | 34.5572 | 35.2484 | 35.9534 | 36.6724 | 37.4059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check central SCADA/network manager | Preventive | Electrical | 1 | 0 | 0 | N/A | NCU | Network/IT | 33.25 | 1 | 1 | interval | 1 | 0.25 | 0 | 8.3125 | 0 | 8.3125 | 0 | 0 | 10.3006 | 104.4587 | 0.07582% | 8.4787 | 8.6483 | 8.8213 | 8.9977 | 9.1777 | 9.3612 | 9.5484 | 9.7394 | 9.9342 | 10.1329 | 10.3355 | 10.5423 | 10.7531 | 10.9682 | 11.1875 | 11.4113 | 11.6395 | 11.8723 | 12.1097 | 12.3519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AC disconnect box inspection | Preventive | Electrical | 1 | 0 | 0 | N/A | Disconnect Box | Inspector | 25.1731 | 1 | 1 | interval | 1 | 0.25 | 0 | 6.2933 | 0 | 6.2933 | 0 | 0 | 7.7984 | 79.0841 | 0.0574% | 6.4191 | 6.5475 | 6.6785 | 6.812 | 6.9483 | 7.0872 | 7.229 | 7.3736 | 7.521 | 7.6715 | 7.8249 | 7.9814 | 8.141 | 8.3038 | 8.4699 | 8.6393 | 8.8121 | 8.9883 | 9.1681 | 9.3515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DC circuit test & combiner box inspection | Preventive | Electrical | 1 | 0 | 0 | N/A | Combiner Box | PV module/array Specialist | 24.0385 | 1 | 1 | interval | 18 | 0.083333 | 0 | 36.0577 | 0 | 36.0577 | 0 | 0 | 44.6815 | 453.1176 | 0.3289% | 36.7788 | 37.5144 | 38.2647 | 39.03 | 39.8106 | 40.6068 | 41.419 | 42.2473 | 43.0923 | 43.9541 | 44.8332 | 45.7299 | 46.6445 | 47.5774 | 48.5289 | 49.4995 | 50.4895 | 51.4993 | 52.5292 | 53.5798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV module electrical connection check | Preventive | Electrical | 1 | 0 | 0 | N/A | PV Module | PV module/array Specialist | 24.0385 | 5 | 1 | Interval | 1442.623 | 0.0041667 | 0 | 144.4935 | 0 | 144.4935 | 0 | 0 | 37.2424 | 329.2531 | 0.239% | 0 | 0 | 0 | 0 | 159.5325 | 0 | 0 | 0 | 0 | 176.1368 | 0 | 0 | 0 | 0 | 194.4692 | 0 | 0 | 0 | 0 | 214.7097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check grounding hardware | Preventive | Electrical | 1 | 0 | 0 | N/A | Structure | Master electrician | 23.1971 | 1 | 1 | interval | 1 | 0.00055556 | 0 | 0.012887 | 0 | 0.012887 | 0 | 0 | 0.015969 | 0.16195 | 0.0001175% | 0.013145 | 0.013408 | 0.013676 | 0.01395 | 0.014229 | 0.014513 | 0.014803 | 0.0151 | 0.015402 | 0.01571 | 0.016024 | 0.016344 | 0.016671 | 0.017005 | 0.017345 | 0.017691 | 0.018045 | 0.018406 | 0.018774 | 0.01915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Corrosion inpsection | Preventive | Mechanical | 1 | 0 | 0 | N/A | connection | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 259.3947 | 0 | 0 | 321.4331 | 3259.6732 | 2.366% | 264.5826 | 269.8742 | 275.2717 | 280.7772 | 286.3927 | 292.1206 | 297.963 | 303.9222 | 310.0007 | 316.2007 | 322.5247 | 328.9752 | 335.5547 | 342.2658 | 349.1111 | 356.0933 | 363.2152 | 370.4795 | 377.8891 | 385.4469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Galvanazation inspection | Preventive | Mechanical | 1 | 0 | 0 | N/A | connection | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 259.3947 | 0 | 0 | 321.4331 | 3259.6732 | 2.366% | 264.5826 | 269.8742 | 275.2717 | 280.7772 | 286.3927 | 292.1206 | 297.963 | 303.9222 | 310.0007 | 316.2007 | 322.5247 | 328.9752 | 335.5547 | 342.2658 | 349.1111 | 356.0933 | 363.2152 | 370.4795 | 377.8891 | 385.4469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV module torque check & visual inspection | Preventive | Mechanical | 1 | 0 | 0 | N/A | Rail/ Fastener | PV module/array Specialist | 24.0385 | 5 | 1 | interval | 1648.7119 | 0.0083333 | 0 | 330.2708 | 0 | 330.2708 | 0 | 0 | 85.1255 | 752.5785 | 0.5462% | 0 | 0 | 0 | 0 | 364.6457 | 0 | 0 | 0 | 0 | 402.5983 | 0 | 0 | 0 | 0 | 444.501 | 0 | 0 | 0 | 0 | 490.7651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Racking torque check & inspection | Preventive | Mechanical | 1 | 0 | 0 | N/A | Structure | Inspector | 25.1731 | 5 | 1 | interval | 103.0445 | 0.0083333 | 0 | 21.6162 | 0 | 21.6162 | 0 | 0 | 5.5715 | 49.2563 | 0.03575% | 0 | 0 | 0 | 0 | 23.8661 | 0 | 0 | 0 | 0 | 26.3501 | 0 | 0 | 0 | 0 | 29.0926 | 0 | 0 | 0 | 0 | 32.1206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor available by email and phone 24x7x365 | Preventive | PV Array | 1 | 0 | 0 | N/A | 0 | Administrator | 16.6635 | 1 | 1 | interval | 1 | 12 | 0 | 199.9615 | 0 | 199.9615 | 0 | 0 | 247.7855 | 2512.8087 | 1.824% | 203.9608 | 208.04 | 212.2008 | 216.4448 | 220.7737 | 225.1892 | 229.693 | 234.2868 | 238.9725 | 243.752 | 248.627 | 253.5996 | 258.6716 | 263.845 | 269.1219 | 274.5043 | 279.9944 | 285.5943 | 291.3062 | 297.1323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test open circuit voltage or IV curve of series strings of modules | Preventive | PV Array | 1 | 0 | 0 | N/A | strings | PV module/array Specialist | 24.0385 | 1 | 1 | interval | 103.0445 | 0.15 | 0 | 371.5547 | 0 | 371.5547 | 0 | 0 | 460.4179 | 4669.1271 | 3.389% | 378.9858 | 386.5655 | 394.2968 | 402.1827 | 410.2264 | 418.4309 | 426.7995 | 435.3355 | 444.0422 | 452.9231 | 461.9815 | 471.2212 | 480.6456 | 490.2585 | 500.0637 | 510.0649 | 520.2662 | 530.6716 | 541.285 | 552.1107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Use infrared camera to inspect for hot spots; bypass diode failure | Preventive | PV Module | 1 | 0 | 0 | N/A | strings | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.15 | 0 | 389.0921 | 0 | 389.0921 | 0 | 0 | 482.1496 | 4889.5099 | 3.549% | 396.8739 | 404.8114 | 412.9076 | 421.1658 | 429.5891 | 438.1809 | 446.9445 | 455.8834 | 465.001 | 474.301 | 483.7871 | 493.4628 | 503.3321 | 513.3987 | 523.6667 | 534.14 | 544.8228 | 555.7193 | 566.8337 | 578.1703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test modules showing corrosion of ribbons to junction box | Preventive | PV Module | 1 | 0 | 0 | N/A | modules | Journeyman electrician | 14.4231 | 5 | 1 | interval | 1443 | 0.08 | 0 | 1665 | 0 | 1665 | 0 | 0 | 429.1447 | 3793.9872 | 2.754% | 0 | 0 | 0 | 0 | 1838.2945 | 0 | 0 | 0 | 0 | 2029.6257 | 0 | 0 | 0 | 0 | 2240.8708 | 0 | 0 | 0 | 0 | 2474.1024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test output of modules that exhibit cracked glass, bubble formation oxidation of busbars, discoloration of busbars, or PV module hot spots (bypass diode failure) | Preventive | PV Module | 1 | 0 | 0 | N/A | modules | Journeyman electrician | 14.4231 | 5 | 1 | interval | 1443 | 0.08 | 0 | 1665 | 0 | 1665 | 0 | 0 | 429.1447 | 3793.9872 | 2.754% | 0 | 0 | 0 | 0 | 1838.2945 | 0 | 0 | 0 | 0 | 2029.6257 | 0 | 0 | 0 | 0 | 2240.8708 | 0 | 0 | 0 | 0 | 2474.1024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meet with key site staff to continue awareness, question any issues, and report on findings. | Administration | Documents | 1 | 0 | 0 | N/A | 0 | Administrator | 16.6635 | 1 | 1 | interval | 1 | 2 | 0 | 33.3269 | 0 | 33.3269 | 0 | 0 | 41.2976 | 418.8015 | 0.304% | 33.9935 | 34.6733 | 35.3668 | 36.0741 | 36.7956 | 37.5315 | 38.2822 | 39.0478 | 39.8288 | 40.6253 | 41.4378 | 42.2666 | 43.1119 | 43.9742 | 44.8537 | 45.7507 | 46.6657 | 47.5991 | 48.551 | 49.5221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate line-to-line fault | Corrective | AC Wiring | 1 | 1 | 1 | EPC | 0 | Master electrician | 23.1971 | 25 | 1 | Weibull | 1 | 1 | 0 | 23.1971 | 0 | 23.1971 | 0 | 0 | 0.33981 | 2.4537 | 0.001781% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74303 | 0.72817 | 0.71361 | 0.69934 | 0.68536 | 0.67166 | 0.65823 | 0.64507 | 0.63217 | 0.61953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate underground AC wiring | Corrective | AC Wiring | 1 | 1 | 1 | N/A | 0 | Utilities locator | 18.5144 | 25 | 3 | Weibull | 1 | 4 | 0 | 74.0577 | 0 | 74.0577 | 0 | 0 | 2.1087 | 15.8036 | 0.01147% | 0.014503 | 0.059144 | 0.13557 | 0.24525 | 0.38935 | 0.56855 | 0.78295 | 1.0319 | 1.3137 | 1.6258 | 1.9646 | 2.3249 | 2.7008 | 3.085 | 3.4694 | 3.8447 | 4.2016 | 4.5302 | 4.821 | 5.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair line-to-line fault | Corrective | AC Wiring | 1 | 1 | 1 | N/A | 0 | Master electrician | 23.1971 | 25 | 1 | Weibull | 1 | 1 | 20 | 23.1971 | 20 | 43.1971 | 0 | 0 | 1.4072 | 15.5694 | 0.0113% | 1.6933 | 1.6595 | 1.6263 | 1.5938 | 1.5619 | 1.5307 | 1.5001 | 1.4701 | 1.4407 | 1.4119 | 1.3837 | 1.356 | 1.3289 | 1.3023 | 1.2763 | 1.2507 | 1.2257 | 1.2012 | 1.1772 | 1.1537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace broken/crushed AC wiring conduit and fittings | Corrective | AC wiring | 1 | 1 | 1 | N/A | strings | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 103.0445 | 0.25 | 10 | 371.5547 | 1030.445 | 1401.9996 | 0 | 0 | 45.6717 | 505.3188 | 0.3668% | 54.9587 | 53.8598 | 52.7829 | 51.7275 | 50.6932 | 49.6796 | 48.6863 | 47.7128 | 46.7588 | 45.8239 | 44.9076 | 44.0097 | 43.1298 | 42.2674 | 41.4223 | 40.594 | 39.7824 | 38.9869 | 38.2074 | 37.4434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate underground DC wiring | Corrective | DC wiring | 1 | 1 | 1 | N/A | 0 | Utilities locator | 18.5144 | 25 | 1 | Weibull | 1 | 2 | 0 | 37.0288 | 0 | 37.0288 | 0 | 0 | 1.2063 | 13.3462 | 0.009687% | 1.4515 | 1.4225 | 1.3941 | 1.3662 | 1.3389 | 1.3121 | 1.2859 | 1.2602 | 1.235 | 1.2103 | 1.1861 | 1.1624 | 1.1391 | 1.1163 | 1.094 | 1.0721 | 1.0507 | 1.0297 | 1.0091 | 0.98894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace broken/crushed DC wiring conduit and fittings | Corrective | DC wiring | 1 | 1 | 1 | N/A | 0 | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 1 | 4 | 100 | 57.6923 | 100 | 157.6923 | 0 | 0 | 5.137 | 56.8366 | 0.04125% | 6.1816 | 6.058 | 5.9368 | 5.8181 | 5.7018 | 5.5878 | 5.4761 | 5.3666 | 5.2593 | 5.1541 | 5.0511 | 4.9501 | 4.8511 | 4.7541 | 4.659 | 4.5659 | 4.4746 | 4.3851 | 4.2974 | 4.2115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace failed DC fuses in combiner box | Corrective | DC wiring | 1 | 1 | 1 | N/A | strings | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 103.0445 | 0.08 | 1 | 118.8975 | 103.0445 | 221.942 | 0 | 0 | 7.23 | 79.9939 | 0.05806% | 8.7002 | 8.5262 | 8.3557 | 8.1887 | 8.0249 | 7.8645 | 7.7072 | 7.5531 | 7.4021 | 7.2541 | 7.1091 | 6.9669 | 6.8276 | 6.6911 | 6.5573 | 6.4262 | 6.2977 | 6.1718 | 6.0484 | 5.9274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-route conduit | Corrective | DC wiring | 1 | 1 | 1 | N/A | 0 | Journeyman electrician | 14.4231 | 25 | 1 | Weibull | 1 | 4 | 100 | 57.6923 | 100 | 157.6923 | 0 | 0 | 5.137 | 56.8366 | 0.04125% | 6.1816 | 6.058 | 5.9368 | 5.8181 | 5.7018 | 5.5878 | 5.4761 | 5.3666 | 5.2593 | 5.1541 | 5.0511 | 4.9501 | 4.8511 | 4.7541 | 4.659 | 4.5659 | 4.4746 | 4.3851 | 4.2974 | 4.2115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracking controller power supply fan filter | Corrective | Tracker | 0 | 1 | 1 | EPC | Controller | Mechanic | 21.2308 | 2 | 1 | interval | 103.0445 | 0.16667 | 25 | 364.619 | 2576.1124 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RE-install inverter control software | Corrective | Inverter | 1 | 1 | 1 | EPC | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 0 | 24.0385 | 0 | 24.0385 | 0 | 0 | 0.37775 | 2.7427 | 0.001991% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86222 | 0.83657 | 0.81168 | 0.78754 | 0.76411 | 0.74139 | 0.71933 | 0.69793 | 0.67717 | 0.65703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace 24VDC power supply for inverter controls | Corrective | Inverter | 1 | 1 | 1 | EPC | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 120 | 24.0385 | 120 | 144.0385 | 0 | 0 | 2.2635 | 16.434 | 0.01193% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1664 | 5.0127 | 4.8636 | 4.7189 | 4.5786 | 4.4424 | 4.3102 | 4.182 | 4.0576 | 3.9369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace AC contactor in inverter | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 2 | 40 | 48.0769 | 40 | 88.0769 | 0 | 0 | 1.3841 | 10.0491 | 0.007294% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1592 | 3.0652 | 2.974 | 2.8855 | 2.7997 | 2.7164 | 2.6356 | 2.5572 | 2.4812 | 2.4074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace capacitors in inverter | Corrective | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 2 | 20000 | 48.0769 | 20000 | 20048.0769 | 0 | 0 | 316.0646 | 2301.968 | 1.671% | 2.3323 | 2.263 | 2.1956 | 2.1303 | 2.067 | 2.0055 | 1.9458 | 1.8879 | 1.8318 | 1.7773 | 719.089 | 697.699 | 676.9452 | 656.8088 | 637.2714 | 618.3151 | 599.9228 | 582.0775 | 564.763 | 547.9636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace DC contactor in inverter | Corrective | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 2 | 40 | 48.0769 | 40 | 88.0769 | 0 | 0 | 2.4059 | 24.6434 | 0.01789% | 2.3323 | 2.263 | 2.1956 | 2.1303 | 2.067 | 2.0055 | 1.9458 | 1.8879 | 1.8318 | 1.7773 | 3.1592 | 3.0652 | 2.974 | 2.8855 | 2.7997 | 2.7164 | 2.6356 | 2.5572 | 2.4812 | 2.4074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace fuses internal to inverter | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 0.25 | 25 | 6.0096 | 25 | 31.0096 | 0 | 0 | 0.4873 | 3.538 | 0.002568% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1123 | 1.0792 | 1.0471 | 1.0159 | 0.98571 | 0.95639 | 0.92794 | 0.90034 | 0.87355 | 0.84757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace GFI components in inveter | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 120 | 24.0385 | 120 | 144.0385 | 0 | 0 | 2.2635 | 16.434 | 0.01193% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1664 | 5.0127 | 4.8636 | 4.7189 | 4.5786 | 4.4424 | 4.3102 | 4.182 | 4.0576 | 3.9369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace IGBT driver card/board; diagnose with fault code | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 2 | 1000 | 48.0769 | 1000 | 1048.0769 | 0 | 0 | 16.4699 | 119.5797 | 0.08679% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.5927 | 36.4744 | 35.3895 | 34.3368 | 33.3154 | 32.3244 | 31.3629 | 30.4299 | 29.5248 | 28.6465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace IGBT matrix in inverter | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 4 | 80000 | 96.1538 | 80000 | 80096.1538 | 0 | 0 | 1258.6601 | 9138.5242 | 6.633% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2872.9072 | 2787.4497 | 2704.5343 | 2624.0852 | 2546.0292 | 2470.2951 | 2396.8137 | 2325.5181 | 2256.3433 | 2189.2261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inductors (coils) in inverter | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 4 | 20000 | 96.1538 | 20000 | 20096.1538 | 0 | 0 | 315.7983 | 2292.859 | 1.664% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720.8134 | 699.3721 | 678.5686 | 658.3839 | 638.7996 | 619.7979 | 601.3614 | 583.4733 | 566.1173 | 549.2776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter control card (PWM signal, voltage, phase, frequency, shut-down); diagnose with fault code | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 1000 | 24.0385 | 1000 | 1024.0385 | 0 | 0 | 16.0921 | 116.8371 | 0.0848% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.7304 | 35.6379 | 34.5778 | 33.5492 | 32.5513 | 31.583 | 30.6435 | 29.732 | 28.8476 | 27.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter data acquisition card/board (also called system input module); diagnose with fault code | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 1000 | 24.0385 | 1000 | 1024.0385 | 0 | 0 | 16.0921 | 116.8371 | 0.0848% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.7304 | 35.6379 | 34.5778 | 33.5492 | 32.5513 | 31.583 | 30.6435 | 29.732 | 28.8476 | 27.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter relay/switch | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 55 | 24.0385 | 55 | 79.0385 | 0 | 0 | 1.242 | 9.0178 | 0.006545% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.835 | 2.7506 | 2.6688 | 2.5894 | 2.5124 | 2.4377 | 2.3652 | 2.2948 | 2.2265 | 2.1603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace maximum power point tracker card/board; diagnose with fault code | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 1000 | 24.0385 | 1000 | 1024.0385 | 0 | 0 | 16.0921 | 116.8371 | 0.0848% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.7304 | 35.6379 | 34.5778 | 33.5492 | 32.5513 | 31.583 | 30.6435 | 29.732 | 28.8476 | 27.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace overvoltage surge suppressors for inverter | Corrective | Inverter | 1 | 1 | 1 | Inverter | inverter | Inverter specialist | 24.0385 | 20 | 1 | Weibull | 1 | 1 | 25 | 24.0385 | 25 | 49.0385 | 0 | 0 | 0.77061 | 5.595 | 0.004061% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7589 | 1.7066 | 1.6558 | 1.6066 | 1.5588 | 1.5124 | 1.4674 | 1.4238 | 1.3814 | 1.3403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace terminal block | Corrective | Inverter | 1 | 1 | 1 | Inverter | Combiner Box | Journeyman electrician | 14.4231 | 5 | 3 | Interval | 18 | 0.25 | 10 | 64.9038 | 180 | 244.9038 | 0 | 0 | 34.6761 | 213.5076 | 0.155% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.6083 | 0 | 0 | 0 | 0 | 363.9142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Restore lost internet connection | Corrective | Monitoring | 1 | 1 | 1 | N/A | Site | Network/IT | 33.25 | 20 | 3 | Interval | 1 | 1 | 0 | 33.25 | 0 | 33.25 | 0 | 0 | 2.4704 | 12.7679 | 0.009267% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Excavate and replace failed foundation element | Corrective | PV Array | 1 | 1 | 1 | N/A | 0 | Structural engineer | 40.4519 | 25 | 3 | Weibull | 103.0445 | 4 | 400 | 16673.3922 | 41217.7986 | 57891.1908 | 0 | 0 | 1648.3766 | 12353.7495 | 8.966% | 11.3367 | 46.233 | 105.9757 | 191.7147 | 304.3548 | 444.4404 | 612.0366 | 806.6109 | 1026.9229 | 1270.9269 | 1535.6987 | 1817.3927 | 2111.2389 | 2411.5881 | 2712.0094 | 3005.4446 | 3284.4178 | 3541.2963 | 3768.5937 | 3959.2996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair roof leaks | Corrective | Roof | 0 | 1 | 1 | N/A | acres | Roofing | 16.4519 | 25 | 1 | Weibull | 2.3153 | 8 | 400 | 304.7263 | 926.1115 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-roof (new roof) | Corrective | Roof | 0 | 1 | 1 | N/A | acres | Roofing | 16.4519 | 30 | 4 | Weibull | 2.3153 | 24 | 75000 | 914.1789 | 173645.9016 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair/replace tracker drive shaft | Corrective | Tracker | 0 | 1 | 1 | N/A | row | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 0.5 | 120 | 1093.857 | 12365.3396 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace hydraulic cylinder | Corrective | Tracker | 0 | 1 | 1 | N/A | 0 | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 0.5 | 120 | 1093.857 | 12365.3396 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracker drive bearing | Corrective | Tracker | 0 | 1 | 1 | N/A | row | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 0.5 | 40 | 1093.857 | 4121.7799 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracker motor controller | Corrective | Tracker | 0 | 1 | 1 | N/A | 0 | Journeyman electrician | 14.4231 | 25 | 3 | Weibull | 103.0445 | 0.5 | 250 | 743.1093 | 25761.1241 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracker mount bearing | Corrective | Tracker | 0 | 1 | 1 | N/A | 0 | Mechanic | 21.2308 | 25 | 3 | Weibull | 103.0445 | 0.5 | 40 | 1093.857 | 4121.7799 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace/upgrade tracker control software | Corrective | Tracker | 0 | 1 | 1 | N/A | 0 | Network/IT | 33.25 | 25 | 3 | Weibull | 103.0445 | 1 | 0 | 3426.2295 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace transformer | Corrective | Transformer | 1 | 0 | 0 | N/A | Transformer | Master electrician | 23.1971 | 50 | 2 | Weibull | 1 | 4 | 22000 | 92.7885 | 22000 | 22092.7885 | 0 | 0 | 223.9212 | 1846.9975 | 1.341% | 18.0205 | 36.7177 | 56.0659 | 76.0364 | 96.5981 | 117.7169 | 139.3566 | 161.4782 | 184.0405 | 207.0001 | 230.3113 | 253.9268 | 277.7972 | 301.8716 | 326.0978 | 350.4221 | 374.7899 | 399.1458 | 423.4335 | 447.5967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-tap transformer | Corrective | Transformer | 1 | 0 | 0 | N/A | Transformer | Master electrician | 23.1971 | 25 | 3 | Weibull | 1 | 2 | 0 | 46.3942 | 0 | 46.3942 | 0 | 0 | 1.321 | 9.9003 | 0.007186% | 0.0090853 | 0.037051 | 0.084929 | 0.15364 | 0.24391 | 0.35618 | 0.49049 | 0.64642 | 0.82298 | 1.0185 | 1.2307 | 1.4565 | 1.692 | 1.9327 | 2.1734 | 2.4086 | 2.6321 | 2.838 | 3.0202 | 3.173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Snow Removal | Preventive | Cleaning/Veg | 0 | 0 | 0 | N/A | acres | Mower/Trimmer | 21.2308 | 0.5 | 1 | interval | 1 | 2 | 100 | 42.4615 | 100 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Array cleaning | Preventive | Cleaning/Veg | 1 | 0 | 0 | N/A | Acre | Cleaner | 10.6779 | 0.25 | 1 | interval | 1 | 4 | 120 | 42.7115 | 120 | 162.7115 | 2 gal fuel/acre @$4/gal + 500 gal H2O/acre @$0.40/gal | 0 | 806.5063 | 8178.8324 | 5.936% | 663.8631 | 677.1403 | 690.6831 | 704.4968 | 718.5867 | 732.9585 | 747.6176 | 762.57 | 777.8214 | 793.3778 | 809.2454 | 825.4303 | 841.9389 | 858.7777 | 875.9532 | 893.4723 | 911.3417 | 929.5686 | 948.1599 | 967.1231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
General Cleaning/Veg Mobilization | Preventive | Cleaning/Veg | 1 | 0 | 0 | N/A | Site | Mower/Trimmer | 21.2308 | 1 | 1 | interval | 1 | 4 | 120 | 84.9231 | 120 | 204.9231 | Other cost = water truckr rental | 0 | 253.9337 | 2575.1577 | 1.869% | 209.0215 | 213.202 | 217.466 | 221.8153 | 226.2516 | 230.7767 | 235.3922 | 240.1 | 244.902 | 249.8001 | 254.7961 | 259.892 | 265.0899 | 270.3916 | 275.7995 | 281.3155 | 286.9418 | 292.6806 | 298.5342 | 304.5049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation management (mowing, trimming) per acre | Preventive | Cleaning/Veg | 1 | 0 | 0 | N/A | Acre | Mower/Trimmer | 21.2308 | 0.25 | 1 | interval | 2.3153 | 2 | 0 | 98.3103 | 0 | 98.3103 | Other cost = 1 gal fuel/acre @ $4/gal + $10/acre mowing consumables | 0 | 487.291 | 4941.6497 | 3.587% | 401.106 | 409.1281 | 417.3107 | 425.6569 | 434.17 | 442.8534 | 451.7105 | 460.7447 | 469.9596 | 479.3588 | 488.946 | 498.7249 | 508.6994 | 518.8734 | 529.2509 | 539.8359 | 550.6326 | 561.6452 | 572.8781 | 584.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Look for any signs of intrusion by pests such as insects and rodents. Remove any nests from electrical boxes (junction boxes, pull boxes, combiner boxes) or around the array. Use safe sanitation practices because pests may carry disease. | Preventive | DC Wiring | 1 | 0 | 0 | N/A | 0 | Pest control | 14.5865 | 1 | 1 | interval | 37 | 0.15 | 1 | 80.9553 | 37 | 117.9553 | 0 | 0 | 146.1662 | 1482.2804 | 1.076% | 120.3144 | 122.7207 | 125.1751 | 127.6786 | 130.2322 | 132.8368 | 135.4935 | 138.2034 | 140.9675 | 143.7868 | 146.6626 | 149.5958 | 152.5877 | 155.6395 | 158.7523 | 161.9273 | 165.1659 | 168.4692 | 171.8386 | 175.2754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Open each combiner box and check that no fuses have blown and that all electrical connections are tight. Use an infrared camera for identifying loose connections because they are warmer than good connections when passing current. | Preventive | DC Wiring | 1 | 0 | 0 | N/A | Combiner Box | Journeyman electrician | 14.4231 | 1 | 1 | interval | 18 | 0.15 | 0 | 38.9423 | 0 | 38.9423 | 0 | 0 | 48.256 | 489.367 | 0.3552% | 39.7212 | 40.5156 | 41.3259 | 42.1524 | 42.9955 | 43.8554 | 44.7325 | 45.6271 | 46.5397 | 47.4705 | 48.4199 | 49.3883 | 50.376 | 51.3835 | 52.4112 | 53.4594 | 54.5286 | 55.6192 | 56.7316 | 57.8662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-torque all electrical connections in combiner box. | Preventive | DC Wiring | 1 | 0 | 0 | N/A | Combiner Box | Journeyman electrician | 14.4231 | 1 | 1 | interval | 18 | 0.25 | 0 | 64.9038 | 0 | 64.9038 | 0 | 0 | 80.4266 | 815.6116 | 0.592% | 66.2019 | 67.526 | 68.8765 | 70.254 | 71.6591 | 73.0923 | 74.5541 | 76.0452 | 77.5661 | 79.1174 | 80.6998 | 82.3138 | 83.96 | 85.6392 | 87.352 | 89.0991 | 90.8811 | 92.6987 | 94.5526 | 96.4437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test system grounding with "megger" | Preventive | DC Wiring | 1 | 0 | 0 | N/A | strings | Master electrician | 23.1971 | 5 | 1 | interval | 103.0445 | 0.25 | 0 | 597.5838 | 0 | 597.5838 | 0 | 0 | 154.024 | 1361.6968 | 0.9883% | 0 | 0 | 0 | 0 | 659.7808 | 0 | 0 | 0 | 0 | 728.4513 | 0 | 0 | 0 | 0 | 804.2691 | 0 | 0 | 0 | 0 | 887.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Calibrate or replace weather sensors & meters | Preventive | Electrical | 1 | 0 | 0 | N/A | Weather Station | Network/IT | 33.25 | 5 | 1 | interval | 1 | 0.5 | 500 | 16.625 | 500 | 516.625 | 0 | 0 | 133.1573 | 1177.2184 | 0.8544% | 0 | 0 | 0 | 0 | 570.3957 | 0 | 0 | 0 | 0 | 629.763 | 0 | 0 | 0 | 0 | 695.3092 | 0 | 0 | 0 | 0 | 767.6776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check Electrical connections & enclosure for tracking motor/controller | Preventive | Tracker | 0 | 0 | 0 | N/A | Controller | Inspector | 25.1731 | 1 | 1 | interval | 1 | 0.083333 | 0 | 2.0978 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check Electrical connections (motor) | Preventive | Tracker | 0 | 0 | 0 | N/A | Motor | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.083333 | 0 | 216.1623 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check Grounding Braids for wear | Preventive | Tracker | 0 | 0 | 0 | N/A | Structure | Inspector | 25.1731 | 1 | 1 | interval | 206.089 | 0.004 | 0 | 20.7516 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrical labor mobilization | Preventive | Electrical | 1 | 1 | 1 | EPC | Site | Master electrician | 23.1971 | 1 | 1 | interval | 1 | 1 | 0 | 23.1971 | 0 | 23.1971 | 0 | 0 | 15.791 | 111.5278 | 0.08095% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.8427 | 29.4196 | 30.0079 | 30.6081 | 31.2203 | 31.8447 | 32.4816 | 33.1312 | 33.7938 | 34.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transformer/switchgear inspection | Preventive | Electrical | 1 | 0 | 0 | N/A | Transformer | Inspector | 25.1731 | 1 | 1 | interval | 1 | 2 | 0 | 50.3462 | 0 | 50.3462 | 0 | 0 | 62.3872 | 632.6729 | 0.4592% | 51.3531 | 52.3801 | 53.4277 | 54.4963 | 55.5862 | 56.6979 | 57.8319 | 58.9885 | 60.1683 | 61.3717 | 62.5991 | 63.8511 | 65.1281 | 66.4307 | 67.7593 | 69.1145 | 70.4968 | 71.9067 | 73.3448 | 74.8117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Clean (vacuum) dust from heat rejection fins | Preventive | Inverter | 1 | 0 | 0 | N/A | inverter | Cleaner | 10.6779 | 1 | 1 | interval | 1 | 0.1 | 0 | 1.0678 | 0 | 1.0678 | 0 | 0 | 1.3232 | 13.4183 | 0.009739% | 1.0891 | 1.1109 | 1.1331 | 1.1558 | 1.1789 | 1.2025 | 1.2266 | 1.2511 | 1.2761 | 1.3016 | 1.3277 | 1.3542 | 1.3813 | 1.4089 | 1.4371 | 1.4658 | 1.4952 | 1.5251 | 1.5556 | 1.5867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Performance test: measure incident light while observing temp and energy output. Calculate PV module efficiency as a function of temp and calculate BOS efficiency. Compare readings with diagnostic benchmark (original efficiency of system). | Preventive | Inverter | 1 | 0 | 0 | N/A | 0 | Inspector | 25.1731 | 1 | 1 | interval | 1 | 1 | 0 | 25.1731 | 0 | 25.1731 | 0 | 0 | 31.1936 | 316.3365 | 0.2296% | 25.6765 | 26.1901 | 26.7139 | 27.2481 | 27.7931 | 28.349 | 28.916 | 29.4943 | 30.0842 | 30.6858 | 31.2996 | 31.9255 | 32.5641 | 33.2153 | 33.8796 | 34.5572 | 35.2484 | 35.9534 | 36.6724 | 37.4059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace any air filters on air-cooled equipment such as inverter. | Preventive | Inverter | 1 | 0 | 0 | N/A | inverter | Inverter specialist | 24.0385 | 1 | 1 | interval | 1 | 0.25 | 25 | 6.0096 | 25 | 31.0096 | 0 | 0 | 38.4261 | 389.6811 | 0.2828% | 31.6298 | 32.2624 | 32.9077 | 33.5658 | 34.2371 | 34.9219 | 35.6203 | 36.3327 | 37.0594 | 37.8005 | 38.5566 | 39.3277 | 40.1142 | 40.9165 | 41.7349 | 42.5696 | 43.4209 | 44.2894 | 45.1752 | 46.0787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace transient voltage surge suppression devices | Preventive | Inverter | 1 | 0 | 0 | Inverter | 0 | Master electrician | 23.1971 | 5 | 1 | interval | 1 | 0.5 | 105 | 11.5986 | 105 | 116.5986 | 0 | 0 | 30.0526 | 265.6897 | 0.1928% | 0 | 0 | 0 | 0 | 128.7342 | 0 | 0 | 0 | 0 | 142.133 | 0 | 0 | 0 | 0 | 156.9263 | 0 | 0 | 0 | 0 | 173.2593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test overvoltage surge suppressors in inverter | Preventive | Inverter | 1 | 0 | 0 | Inverter | inverter | Inverter specialist | 24.0385 | 5 | 1 | interval | 1 | 0.1 | 0 | 2.4038 | 0 | 2.4038 | 0 | 0 | 0.61958 | 5.4776 | 0.003976% | 0 | 0 | 0 | 0 | 2.654 | 0 | 0 | 0 | 0 | 2.9303 | 0 | 0 | 0 | 0 | 3.2353 | 0 | 0 | 0 | 0 | 3.572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Anemometer inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | 0 | Inspector | 25.1731 | 1 | 1 | interval | 1 | 0.1 | 0 | 2.5173 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Driveshaft torque check & visual inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | Driveshaft | Inspector | 25.1731 | 1 | 1 | interval | 0 | 0.0083333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gearbox lubrication | Preventive | Tracker | 0 | 0 | 0 | N/A | block | Mechanic | 21.2308 | 0.5 | 1 | interval | 103.0445 | 0.25 | 0 | 546.9285 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inclinometer inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | 0 | Inspector | 25.1731 | 1 | 1 | interval | 1 | 0.1 | 0 | 2.5173 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Limit switch inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | block | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical labor mobilization | Preventive | Mechanical | 0 | 0 | 0 | EPC | Site | Mechanic | 21.2308 | 1 | 1 | interval | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Module table inpsection | Preventive | Tracker | 0 | 0 | 0 | N/A | connection | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Screw jack greasing | Preventive | Tracker | 0 | 0 | 0 | N/A | block | Mechanic | 21.2308 | 0.5 | 1 | interval | 103.0445 | 0.25 | 0 | 546.9285 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Screw jack inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | block | Inspector | 25.1731 | 0.5 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slew gear lubrication | Preventive | Tracker | 0 | 0 | 0 | N/A | Slew Gear | Mechanic | 21.2308 | 3 | 1 | interval | 0 | 0.25 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slew gear torque check & wear inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | Slew Gear | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.016667 | 0 | 43.2325 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Torque inspection | Preventive | Mechanical | 0 | 0 | 0 | N/A | block | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tracking Controller inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | 0 | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.1 | 0 | 259.3947 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Universal joint greasing (zirc fitting) | Preventive | Tracker | 0 | 0 | 0 | N/A | Driveshaft | Mechanic | 21.2308 | 0.5 | 1 | interval | 0 | 0.16667 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Universal joint inspection | Preventive | Tracker | 0 | 0 | 0 | N/A | Driveshaft | Inspector | 25.1731 | 1 | 1 | interval | 0 | 0.0083333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Spot-check monitoring instruments (pyranometer, etc) with hand-held instruments to ensure that they are operational and within specifications. | Preventive | Monitoring | 0 | 0 | 0 | N/A | 0 | Inspector | 25.1731 | 1 | 1 | interval | 1 | 1 | 0 | 25.1731 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect ballasted, non-penetrating mounting system for abnormal movement | Preventive | PV Array | 0 | 0 | 0 | N/A | rows | Inspector | 25.1731 | 1 | 1 | interval | 103.0445 | 0.08 | 0 | 207.5158 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remove bird nests from array and rack area. | Preventive | PV Array | 0 | 0 | 0 | N/A | Acres | Pest control | 14.5865 | 1 | 1 | interval | 2.3153 | 4 | 0 | 135.0876 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walk through each row of the PV array and check the PV modules for any damage. Report any damage to rack and damaged modules for warranty replacement. Note location and serial number of questionable modules. | Preventive | PV Array | 1 | 0 | 0 | N/A | Acres | Inspector | 25.1731 | 1 | 1 | interval | 2.3153 | 0.5 | 0 | 29.1413 | 0 | 29.1413 | 0 | 0 | 36.111 | 366.2035 | 0.2658% | 29.7242 | 30.3187 | 30.925 | 31.5435 | 32.1744 | 32.8179 | 33.4742 | 34.1437 | 34.8266 | 35.5231 | 36.2336 | 36.9583 | 37.6974 | 38.4514 | 39.2204 | 40.0048 | 40.8049 | 41.621 | 42.4534 | 43.3025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lubricate tracker mounting bearings/gimbals | Preventive | Tracker | 0 | 0 | 0 | N/A | 0 | Mechanic | 21.2308 | 1 | 1 | interval | 103.0445 | 0.15 | 1 | 328.1571 | 103.0445 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect transformer meter, oil and tempertaure gauges | Preventive | Transformer | 0 | 0 | 0 | N/A | 0 | Master electrician | 23.1971 | 1 | 1 | interval | 1 | 0.25 | 0 | 5.7993 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 16682.456 | 137778.286 | 100% | 4404.1281 | 4541.8165 | 4706.8062 | 4900.2543 | 10709.2686 | 5689.952 | 5978.9451 | 6297.5071 | 6644.3934 | 13185.1653 | 21998.5371 | 22564.235 | 23187.7428 | 23858.9051 | 32410.9667 | 25298.5787 | 26042.4737 | 26785.4254 | 27514.858 | 36929.1611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Cleaning
Cleaning Freqency Model
Inputs |  |  |  | Results
Plant size (MWp) | 0.44
Person-hours to clean 1 MWp | 40 |  |  | Cost-minimizing # cleanings/year |  | 14
Hourly cost of cleaning labor | 15
kW cleaned per hour per person | 25 |  |  | AT OPTIMUM CLEANING FREQUENCY
Person-hours per Cleaning | 17.6 |  |  |  | Cleaning labor cost | 5096
Actual hours per cleaning | 8.8 |  |  |  | Lost revenue from soiling | 9096.8127
Labor Cost Per Cleaning | 264 |  |  |  | Lost revenue from on-sun cleaning | 2972.3878
Total Cost Per Cleaning | 364 |  |  |  | TOTAL | 17165.2004
Fixed set-up cost per cleaning | 100
# of cleaners | 2
On-sun hours per year | 2555
kWh per MWp | 1596000
Revenue per kWh generated | 0.2
Soiling loss per day | 0.5%
% of cleaning during "on sun" hours | 50%
Sum of cleaning labor & lost kWh | Cleanings/year | Cost of cleaning set-up and labor | Days between cleanings | % of original power produced right before cleaning | Average Power Output | kWh/year lost to soiling | Value of kWh lost due to soiling | Hours/year of cleaning during "on sun" hours | kWh/year lost to being off-sun for cleaning | Value of kWh lost due to cleaning during "on sun" hrs
76566 | 1 | 364 | 365 | 16.05% | 45.77% | 380817.5979 | 76163.5196 | 4.4 | 194.076 | 38.8152
49671 | 2 | 728 | 183 | 39.96% | 65.29% | 243750.5285 | 48750.1057 | 8.8 | 966.4983 | 193.2997
37129 | 3 | 1092 | 122 | 54.25% | 74.62% | 178216.4492 | 35643.2898 | 13.2 | 1968.2689 | 393.6538
30022 | 4 | 1456 | 91 | 63.37% | 80.1% | 139762.213 | 27952.4426 | 17.6 | 3065.5449 | 613.109
25782 | 5 | 1820 | 73 | 69.36% | 83.54% | 115616.7186 | 23123.3437 | 22 | 4193.7471 | 838.7494
22997 | 6 | 2184 | 61 | 73.66% | 85.94% | 98720.7948 | 19744.159 | 26.4 | 5344.493 | 1068.8986
20974 | 7 | 2548 | 52 | 77.05% | 87.81% | 85608.8491 | 17121.7698 | 30.8 | 6522.9729 | 1304.5946
19779 | 8 | 2912 | 46 | 79.41% | 89.08% | 76650.9388 | 15330.1878 | 35.2 | 7682.4375 | 1536.4875
18858 | 9 | 3276 | 41 | 81.42% | 90.17% | 69050.3268 | 13810.0654 | 39.6 | 8862.09 | 1772.418
18225 | 10 | 3640 | 37 | 83.07% | 91.05% | 62879.359 | 12575.8718 | 44 | 10046.1885 | 2009.2377
17242 | 12 | 4368 | 30 | 86.04% | 92.61% | 51882.7597 | 10376.5519 | 52.8 | 12485.9331 | 2497.1866
17165 | 14 | 5096 | 26 | 87.78% | 93.52% | 45484.0633 | 9096.8127 | 61.6 | 14861.9389 | 2972.3878
17398 | 16 | 5824 | 23 | 89.11% | 94.21% | 40629.228 | 8125.8456 | 70.4 | 17242.4182 | 3448.4836
17636 | 18 | 6552 | 20 | 90.46% | 94.91% | 35725.9535 | 7145.1907 | 79.2 | 19691.6204 | 3938.3241
18186 | 20 | 7280 | 18 | 91.37% | 95.38% | 32429.9237 | 6485.9847 | 88 | 22100.026 | 4420.0052
20481 | 26 | 9464 | 14 | 93.22% | 96.33% | 25771.8952 | 5154.379 | 114.4 | 29311.8894 | 5862.3779
23709 | 33 | 12012 | 11 | 94.64% | 97.05% | 20719.9987 | 4143.9997 | 145.2 | 37767.2327 | 7553.4465
26678 | 39 | 14196 | 9 | 95.59% | 97.53% | 17323.956 | 3464.7912 | 171.6 | 45083.7123 | 9016.7425
33852 | 52 | 18928 | 7 | 96.55% | 98.02% | 13905.2263 | 2781.0453 | 228.8 | 60717.2711 | 12143.4542
38958 | 61 | 22204 | 6 | 97.04% | 98.26% | 12187.3005 | 2437.4601 | 268.4 | 71583.9493 | 14316.7899
45884 | 73 | 26572 | 5 | 97.52% | 98.51% | 10463.6388 | 2092.7278 | 321.2 | 86096.5203 | 17219.3041
56444 | 91 | 33124 | 4 | 98.01% | 98.76% | 8734.2196 | 1746.8439 | 400.4 | 107865.1249 | 21573.025
74875 | 122 | 44408 | 3 | 98.51% | 99% | 6999.0213 | 1399.8043 | 536.8 | 145337.0726 | 29067.4145
Days between cleanings | Loss Factor | Mean Loss Factor
1 | 0.995 | 0.995
2 | 0.99003 | 0.99251
3 | 0.98507 | 0.99003
4 | 0.98015 | 0.98756
5 | 0.97525 | 0.9851
6 | 0.97037 | 0.98265
7 | 0.96552 | 0.9802
8 | 0.96069 | 0.97776
9 | 0.95589 | 0.97533
10 | 0.95111 | 0.97291
11 | 0.94635 | 0.97049
12 | 0.94162 | 0.96809
13 | 0.93691 | 0.96569
14 | 0.93223 | 0.9633
15 | 0.92757 | 0.96092
16 | 0.92293 | 0.95854
17 | 0.91832 | 0.95618
18 | 0.91372 | 0.95382
19 | 0.90916 | 0.95147
20 | 0.90461 | 0.94913
21 | 0.90009 | 0.94679
22 | 0.89559 | 0.94446
23 | 0.89111 | 0.94214
24 | 0.88665 | 0.93983
25 | 0.88222 | 0.93753
26 | 0.87781 | 0.93523
27 | 0.87342 | 0.93294
28 | 0.86905 | 0.93066
29 | 0.86471 | 0.92838
30 | 0.86038 | 0.92612
31 | 0.85608 | 0.92386
32 | 0.8518 | 0.92161
33 | 0.84754 | 0.91936
34 | 0.84331 | 0.91713
35 | 0.83909 | 0.9149
36 | 0.83489 | 0.91267
37 | 0.83072 | 0.91046
38 | 0.82657 | 0.90825
39 | 0.82243 | 0.90605
40 | 0.81832 | 0.90386
41 | 0.81423 | 0.90167
42 | 0.81016 | 0.89949
43 | 0.80611 | 0.89732
44 | 0.80208 | 0.89516
45 | 0.79807 | 0.893
46 | 0.79408 | 0.89085
47 | 0.7901 | 0.8887
48 | 0.78615 | 0.88657
49 | 0.78222 | 0.88444
50 | 0.77831 | 0.88232
51 | 0.77442 | 0.8802
52 | 0.77055 | 0.87809
53 | 0.7667 | 0.87599
54 | 0.76286 | 0.87389
55 | 0.75905 | 0.87181
56 | 0.75525 | 0.86973
57 | 0.75148 | 0.86765
58 | 0.74772 | 0.86558
59 | 0.74398 | 0.86352
60 | 0.74026 | 0.86147
61 | 0.73656 | 0.85942
62 | 0.73288 | 0.85738
63 | 0.72921 | 0.85534
64 | 0.72557 | 0.85332
65 | 0.72194 | 0.8513
66 | 0.71833 | 0.84928
67 | 0.71474 | 0.84727
68 | 0.71116 | 0.84527
69 | 0.70761 | 0.84328
70 | 0.70407 | 0.84129
71 | 0.70055 | 0.83931
72 | 0.69705 | 0.83733
73 | 0.69356 | 0.83536
74 | 0.69009 | 0.8334
75 | 0.68664 | 0.83144
76 | 0.68321 | 0.82949
77 | 0.67979 | 0.82755
78 | 0.67639 | 0.82561
79 | 0.67301 | 0.82368
80 | 0.66965 | 0.82175
81 | 0.6663 | 0.81983
82 | 0.66297 | 0.81792
83 | 0.65965 | 0.81601
84 | 0.65635 | 0.81411
85 | 0.65307 | 0.81222
86 | 0.64981 | 0.81033
87 | 0.64656 | 0.80845
88 | 0.64333 | 0.80657
89 | 0.64011 | 0.8047
90 | 0.63691 | 0.80283
91 | 0.63372 | 0.80098
92 | 0.63056 | 0.79912
93 | 0.6274 | 0.79728
94 | 0.62427 | 0.79544
95 | 0.62114 | 0.7936
96 | 0.61804 | 0.79177
97 | 0.61495 | 0.78995
98 | 0.61187 | 0.78813
99 | 0.60881 | 0.78632
100 | 0.60577 | 0.78452
101 | 0.60274 | 0.78272
102 | 0.59973 | 0.78092
103 | 0.59673 | 0.77913
104 | 0.59375 | 0.77735
105 | 0.59078 | 0.77558
106 | 0.58782 | 0.7738
107 | 0.58488 | 0.77204
108 | 0.58196 | 0.77028
109 | 0.57905 | 0.76852
110 | 0.57615 | 0.76678
111 | 0.57327 | 0.76503
112 | 0.57041 | 0.76329
113 | 0.56756 | 0.76156
114 | 0.56472 | 0.75984
115 | 0.56189 | 0.75811
116 | 0.55908 | 0.7564
117 | 0.55629 | 0.75469
118 | 0.55351 | 0.75298
119 | 0.55074 | 0.75128
120 | 0.54799 | 0.74959
121 | 0.54525 | 0.7479
122 | 0.54252 | 0.74622
123 | 0.53981 | 0.74454
124 | 0.53711 | 0.74287
125 | 0.53442 | 0.7412
126 | 0.53175 | 0.73954
127 | 0.52909 | 0.73788
128 | 0.52645 | 0.73623
129 | 0.52381 | 0.73458
130 | 0.5212 | 0.73294
131 | 0.51859 | 0.7313
132 | 0.516 | 0.72967
133 | 0.51342 | 0.72805
134 | 0.51085 | 0.72643
135 | 0.5083 | 0.72481
136 | 0.50575 | 0.7232
137 | 0.50322 | 0.72159
138 | 0.50071 | 0.71999
139 | 0.49821 | 0.7184
140 | 0.49571 | 0.71681
141 | 0.49324 | 0.71522
142 | 0.49077 | 0.71364
143 | 0.48832 | 0.71206
144 | 0.48587 | 0.71049
145 | 0.48344 | 0.70893
146 | 0.48103 | 0.70737
147 | 0.47862 | 0.70581
148 | 0.47623 | 0.70426
149 | 0.47385 | 0.70271
150 | 0.47148 | 0.70117
151 | 0.46912 | 0.69963
152 | 0.46678 | 0.6981
153 | 0.46444 | 0.69658
154 | 0.46212 | 0.69505
155 | 0.45981 | 0.69354
156 | 0.45751 | 0.69202
157 | 0.45522 | 0.69051
158 | 0.45295 | 0.68901
159 | 0.45068 | 0.68751
160 | 0.44843 | 0.68602
161 | 0.44619 | 0.68453
162 | 0.44396 | 0.68304
163 | 0.44174 | 0.68156
164 | 0.43953 | 0.68009
165 | 0.43733 | 0.67862
166 | 0.43514 | 0.67715
167 | 0.43297 | 0.67569
168 | 0.4308 | 0.67423
169 | 0.42865 | 0.67278
170 | 0.4265 | 0.67133
171 | 0.42437 | 0.66988
172 | 0.42225 | 0.66844
173 | 0.42014 | 0.66701
174 | 0.41804 | 0.66558
175 | 0.41595 | 0.66415
176 | 0.41387 | 0.66273
177 | 0.4118 | 0.66131
178 | 0.40974 | 0.6599
179 | 0.40769 | 0.65849
180 | 0.40565 | 0.65708
181 | 0.40362 | 0.65568
182 | 0.40161 | 0.65429
183 | 0.3996 | 0.6529
184 | 0.3976 | 0.65151
185 | 0.39561 | 0.65012
186 | 0.39363 | 0.64875
187 | 0.39167 | 0.64737
188 | 0.38971 | 0.646
189 | 0.38776 | 0.64463
190 | 0.38582 | 0.64327
191 | 0.38389 | 0.64191
192 | 0.38197 | 0.64056
193 | 0.38006 | 0.63921
194 | 0.37816 | 0.63786
195 | 0.37627 | 0.63652
196 | 0.37439 | 0.63519
197 | 0.37252 | 0.63385
198 | 0.37066 | 0.63252
199 | 0.3688 | 0.6312
200 | 0.36696 | 0.62988
201 | 0.36512 | 0.62856
202 | 0.3633 | 0.62725
203 | 0.36148 | 0.62594
204 | 0.35967 | 0.62463
205 | 0.35788 | 0.62333
206 | 0.35609 | 0.62203
207 | 0.35431 | 0.62074
208 | 0.35253 | 0.61945
209 | 0.35077 | 0.61817
210 | 0.34902 | 0.61688
211 | 0.34727 | 0.61561
212 | 0.34554 | 0.61433
213 | 0.34381 | 0.61306
214 | 0.34209 | 0.6118
215 | 0.34038 | 0.61053
216 | 0.33868 | 0.60927
217 | 0.33698 | 0.60802
218 | 0.3353 | 0.60677
219 | 0.33362 | 0.60552
220 | 0.33195 | 0.60428
221 | 0.33029 | 0.60304
222 | 0.32864 | 0.6018
223 | 0.327 | 0.60057
224 | 0.32536 | 0.59934
225 | 0.32374 | 0.59812
226 | 0.32212 | 0.5969
227 | 0.32051 | 0.59568
228 | 0.31891 | 0.59446
229 | 0.31731 | 0.59325
230 | 0.31572 | 0.59205
231 | 0.31415 | 0.59084
232 | 0.31258 | 0.58964
233 | 0.31101 | 0.58845
234 | 0.30946 | 0.58726
235 | 0.30791 | 0.58607
236 | 0.30637 | 0.58488
237 | 0.30484 | 0.5837
238 | 0.30331 | 0.58252
239 | 0.3018 | 0.58135
240 | 0.30029 | 0.58018
241 | 0.29879 | 0.57901
242 | 0.29729 | 0.57785
243 | 0.29581 | 0.57668
244 | 0.29433 | 0.57553
245 | 0.29286 | 0.57437
246 | 0.29139 | 0.57322
247 | 0.28994 | 0.57208
248 | 0.28849 | 0.57093
249 | 0.28704 | 0.56979
250 | 0.28561 | 0.56866
251 | 0.28418 | 0.56752
252 | 0.28276 | 0.56639
253 | 0.28135 | 0.56527
254 | 0.27994 | 0.56414
255 | 0.27854 | 0.56302
256 | 0.27715 | 0.56191
257 | 0.27576 | 0.56079
258 | 0.27438 | 0.55968
259 | 0.27301 | 0.55858
260 | 0.27164 | 0.55747
261 | 0.27029 | 0.55637
262 | 0.26893 | 0.55527
263 | 0.26759 | 0.55418
264 | 0.26625 | 0.55309
265 | 0.26492 | 0.552
266 | 0.2636 | 0.55092
267 | 0.26228 | 0.54984
268 | 0.26097 | 0.54876
269 | 0.25966 | 0.54768
270 | 0.25836 | 0.54661
271 | 0.25707 | 0.54554
272 | 0.25579 | 0.54448
273 | 0.25451 | 0.54342
274 | 0.25324 | 0.54236
275 | 0.25197 | 0.5413
276 | 0.25071 | 0.54025
277 | 0.24946 | 0.5392
278 | 0.24821 | 0.53815
279 | 0.24697 | 0.53711
280 | 0.24573 | 0.53607
281 | 0.2445 | 0.53503
282 | 0.24328 | 0.534
283 | 0.24206 | 0.53296
284 | 0.24085 | 0.53194
285 | 0.23965 | 0.53091
286 | 0.23845 | 0.52989
287 | 0.23726 | 0.52887
288 | 0.23607 | 0.52785
289 | 0.23489 | 0.52684
290 | 0.23372 | 0.52583
291 | 0.23255 | 0.52482
292 | 0.23139 | 0.52381
293 | 0.23023 | 0.52281
294 | 0.22908 | 0.52181
295 | 0.22793 | 0.52082
296 | 0.22679 | 0.51982
297 | 0.22566 | 0.51883
298 | 0.22453 | 0.51785
299 | 0.22341 | 0.51686
300 | 0.22229 | 0.51588
301 | 0.22118 | 0.5149
302 | 0.22007 | 0.51392
303 | 0.21897 | 0.51295
304 | 0.21788 | 0.51198
305 | 0.21679 | 0.51101
306 | 0.21571 | 0.51005
307 | 0.21463 | 0.50908
308 | 0.21355 | 0.50813
309 | 0.21249 | 0.50717
310 | 0.21142 | 0.50621
311 | 0.21037 | 0.50526
312 | 0.20932 | 0.50431
313 | 0.20827 | 0.50337
314 | 0.20723 | 0.50243
315 | 0.20619 | 0.50149
316 | 0.20516 | 0.50055
317 | 0.20413 | 0.49961
318 | 0.20311 | 0.49868
319 | 0.2021 | 0.49775
320 | 0.20109 | 0.49682
321 | 0.20008 | 0.4959
322 | 0.19908 | 0.49498
323 | 0.19809 | 0.49406
324 | 0.1971 | 0.49314
325 | 0.19611 | 0.49223
326 | 0.19513 | 0.49132
327 | 0.19415 | 0.49041
328 | 0.19318 | 0.4895
329 | 0.19222 | 0.4886
330 | 0.19126 | 0.4877
331 | 0.1903 | 0.4868
332 | 0.18935 | 0.4859
333 | 0.1884 | 0.48501
334 | 0.18746 | 0.48412
335 | 0.18652 | 0.48323
336 | 0.18559 | 0.48234
337 | 0.18466 | 0.48146
338 | 0.18374 | 0.48058
339 | 0.18282 | 0.4797
340 | 0.18191 | 0.47883
341 | 0.181 | 0.47795
342 | 0.18009 | 0.47708
343 | 0.17919 | 0.47621
344 | 0.1783 | 0.47535
345 | 0.1774 | 0.47448
346 | 0.17652 | 0.47362
347 | 0.17563 | 0.47276
348 | 0.17476 | 0.47191
349 | 0.17388 | 0.47105
350 | 0.17301 | 0.4702
351 | 0.17215 | 0.46935
352 | 0.17129 | 0.46851
353 | 0.17043 | 0.46766
354 | 0.16958 | 0.46682
355 | 0.16873 | 0.46598
356 | 0.16789 | 0.46514
357 | 0.16705 | 0.46431
358 | 0.16621 | 0.46347
359 | 0.16538 | 0.46264
360 | 0.16455 | 0.46182
361 | 0.16373 | 0.46099
362 | 0.16291 | 0.46017
363 | 0.1621 | 0.45935
364 | 0.16129 | 0.45853
365 | 0.16048 | 0.45771