## Introduction
General Information
This excel sheet includes the Annual Maintenance Plan which is based on real examples and has been modified by the Task Force to incorporate different experience and reflect wider requirements.
This product is part of the "O&M Best Practices Guidelines" version 1.0 report and can be considered as an attachment within the scope of the Preventative Maintenance.
Acknowledgements
SolarPower Europe would like to extend special thanks to all the Task Force Members that contributed with their knowledge and experience to the development of this Annual Maintenance Plan.
This work would never have been realized without their continuous support.
Disclaimer
Adherence to the "O&M Best Practices Guidelines" version 1.0 report and its by-products such as this Annual Maintenance Plan is voluntary. SolarPower Europe and the Task Force members hold no responsibility for misinterpretations
or misuse of the content and will provide no indemnities. Any stakeholders that adhere to this version are responsible for self-certifying that they have fulfilled the guide requirements.
Please note that version 1.0 is subject to further changes, updates and improvements
© SOLARPOWER EUROPE 2016

## Annual Maintenance Plan
Plant: Typical 3-5MW site
Site address: land-locked site far from seashore
[7 empty] | Q1 | [12 empty] | Q2 | [12 empty] | Q3 | [12 empty] | Q4
Sub Group | Equipment | Sub unit | Task | Frequency | Importance | O&M Decision on Frequency (by Technical Manager) | W1 | W2 | W3 | W4 | W5 | W6 | W7 | W8 | W9 | W10 | W11 | W12 | W13 | W14 | W15 | W16 | W17 | W18 | W19 | W20 | W21 | W22 | W23 | W24 | W25 | W26 | W27 | W28 | W29 | W30 | W31 | W32 | W33 | W34 | W35 | W36 | W37 | W38 | W39 | W40 | W41 | W42 | W43 | W44 | W45 | W46 | W47 | W48 | W49 | W50 | W51 | W52
Documentation | as -built | AC-System | Complete and correct of documentation AC-System | initial/ ongoing | necessary
Documentation | as -built | Auxiliary Systems | Complete and correct documentation of all auxiliary systems (security, monitoring, ICT, energy supply, civil works, etc.) | initial/ ongoing | necessary
Documentation | as -built | DC-System | Complete and correct of documentation DC-System | initial/ ongoing | necessary
Documentation | as -built | System Documentation (IEC 62443) | System Data, Wiring diagram, mechanical design, O&M information (e.g. Operation and maintenance information shall be provided and shall include, at a minimum, the following items: a) Procedures for verifying correct system operation. b) A checklist of what to do in case of a system failure. c) Emergency shutdown and isolation procedures. d) Maintenance and cleaning recommendations (if any), Test results and commissioning data, | initial/ ongoing | necessary
Documentation | as -built | System Verification | Inspection, Testing 1)Test continuity of equipment grounding conductors and system grounding conductors (if applicable). 2) Test polarity of all dc cables and check for correct cable identification and connection. 3) Test open-circuit voltage [Voc] for each PV source circuit. 4) Test short-circuit current [Isc] for each PV source circuit. 5) Test functionality of major system components (switchgear, controls, inverters), including inverter anti-islanding. 6) Test the insulation resistance of the dc circuit conductors | initial/ ongoing | necessary
Documentation | O&M-Duration | Plant Audit | Audit of a power plant at take-over by O&M contractor, checking O&M reports, faults, repairs, design conformity and changes, monitoring, performance, etc. | initial + 3-5 yrs | necessary
Documentation | O&M-Duration | Log Book | Checking and keeping records for tickets, faults, inspection results, or other events into one log book, as well as feed back and ensuing work plan for internal purpose, client, insurance, etc. | daily | necessary
Documentation | O&M-Duration | Maintenance | Creation of a maintenance protocole (about maintenance done according to manufacturer requirements or at least to mandatory national regulatory regulations) |  | necessary
Documentation | O&M-Duration | Inspection | Creation of an inspection protocole |  | necessary
Documentation | O&M-Duration | Work Plan | Action Plan following Audit, Maintenance Protocole, and Inspection Protocole, in order to monitor or fix issue and inform client | ongoing | necessary
Documentation | O&M-Duration | Report | Ongoing reporting as specified in O&M Contract to inform client about issues, diagnosis, and repairs, as well as plant performance (Summary of failures, losses, KPIs, human activity on site) | monthly/ quarterly/ annually | necessary
Documentation | O&M-Duration |  | Variance analysis | ongoing | necessary
Power Generation | Modules |  | Integrity inspection | Annual | necessary
Power Generation | Modules |  | Cables visual inspection | Annual | necessary
Power Generation | Modules |  | Thermography inspection | Monthly | necessary
Power Generation | Modules |  | Measurements inspection | Annual | necessary
Power Generation | Modules |  | Retightening | Monthly | necessary
Power Generation | Modules |  | Modules cleaning | Annual | necessary
Power Generation | Modules |  | On-Site degradation measurement (with most accurate and available technology) with pre-defined reference modules and strings. NB: accurate module and string selection necessary + stable+high irradiation | Annual | optional/according to client
Power Generation | LV Switchboard | Array/String Junction Box | Integrity inspection | Semi-annual | necessary
Power Generation | LV Switchboard | Array/String Junction Box | Documents inspection | Semi-annual | necessary
Power Generation | LV Switchboard | Array/String Junction Box | Cables visual inspection | Semi-annual | necessary
Power Generation | LV Switchboard | Array/String Junction Box | Labelling and identification | Semi-annual | necessary
Power Generation | LV Switchboard | Array/String Junction Box | Electrical protections visual inspection | Semi-annual | necessary
Power Generation | LV Switchboard | Array/String Junction Box | Thermography inspection | Semi-annual | necessary
Power Generation | LV Switchboard | Array/String Junction Box | Sensors functional verification | Annual | necessary
Power Generation | LV Switchboard | Array/String Junction Box | Measurements inspection | Semi-annual | necessary
Power Generation | LV Switchboard | Array/String Junction Box | Check correct operation | Semi-annual | necessary
Power Generation | LV Switchboard | Array/String Junction Box | Electrical protection correct operation | Semi-annual | necessary
Power Generation | LV Switchboard | Array/String Junction Box | Check fuse status | Semi-annual | necessary
Power Generation | LV Switchboard | Array/String Junction Box | Monitoring operation test | Annual | necessary
Power Generation | LV Switchboard | Array/String Junction Box | Check cables terminals | Semi-annual | necessary
Power Generation | LV Switchboard | Array/String Junction Box | General cleaning | Semi-annual | necessary
Power Generation | LV Switchboard | Generator Junction Box | Integrity inspection | Annual | necessary
Power Generation | LV Switchboard | Generator Junction Box | Documents inspection | Annual | necessary
Power Generation | LV Switchboard | Generator Junction Box | Cables visual inspection | Annual | necessary
Power Generation | LV Switchboard | Generator Junction Box | Labelling and identification | Annual | necessary
Power Generation | LV Switchboard | Generator Junction Box | Electrical protections visual inspection | Annual | necessary
Power Generation | LV Switchboard | Generator Junction Box | Thermography inspection | Semi-annual | necessary
Power Generation | LV Switchboard | Generator Junction Box | Sensors functional verification | Semi-annual | necessary
Power Generation | LV Switchboard | Generator Junction Box | Measurements inspection | Annual | necessary
Power Generation | LV Switchboard | Generator Junction Box | Electrical protection correct operation | Monthly | necessary
Power Generation | LV Switchboard | Generator Junction Box | Check fuse status | Annual | necessary
Power Generation | LV Switchboard | Generator Junction Box | Monitoring operation test | Semi-annual | necessary
Power Generation | LV Switchboard | Generator Junction Box | Check cables terminals | Annual | necessary
Power Generation | LV Switchboard | Generator Junction Box | General cleaning | Annual | necessary
Power Generation | LV Switchboard | AC Combiner Switchboard | Integrity inspection | Semi-annual | necessary
Power Generation | LV Switchboard | AC Combiner Switchboard | Documents inspection | Semi-annual | necessary
Power Generation | LV Switchboard | AC Combiner Switchboard | Cables visual inspection | Annual | necessary
Power Generation | LV Switchboard | AC Combiner Switchboard | Labelling and identification | Annual | necessary
Power Generation | LV Switchboard | AC Combiner Switchboard | Electrical protections visual inspection | Semi-annual | necessary
Power Generation | LV Switchboard | AC Combiner Switchboard | Thermography inspection | Semi-annual | necessary
Power Generation | LV Switchboard | AC Combiner Switchboard | Sensors functional verification | Annual | necessary
Power Generation | LV Switchboard | AC Combiner Switchboard | Measurements inspection | Semi-annual | necessary
Power Generation | LV Switchboard | AC Combiner Switchboard | Check correct operation | Annual | necessary
Power Generation | LV Switchboard | AC Combiner Switchboard | Electrical protection correct operation | Annual | necessary
Power Generation | LV Switchboard | AC Combiner Switchboard | Check fuse status | Annual | necessary
Power Generation | LV Switchboard | AC Combiner Switchboard | Check cables terminals | Monthly | necessary
Power Generation | LV Switchboard | AC Combiner Switchboard | General cleaning | Annual | necessary
Power Generation | LV Switchboard | AUX Switchboard | Integrity inspection | Semi-annual | necessary
Power Generation | LV Switchboard | AUX Switchboard | Documents inspection | Semi-annual | necessary
Power Generation | LV Switchboard | AUX Switchboard | Cables visual inspection | Semi-annual | necessary
Power Generation | LV Switchboard | AUX Switchboard | Labelling and identification | Semi-annual | necessary
Power Generation | LV Switchboard | AUX Switchboard | Electrical protections visual inspection | Semi-annual | necessary
Power Generation | LV Switchboard | AUX Switchboard | Thermography inspection | Semi-annual | necessary
Power Generation | LV Switchboard | AUX Switchboard | Measurements inspection | Semi-annual | necessary
Power Generation | LV Switchboard | AUX Switchboard | Electrical protection correct operation | Semi-annual | necessary
Power Generation | LV Switchboard | AUX Switchboard | Check fuse status | Semi-annual | necessary
Power Generation | LV Switchboard | AUX Switchboard | Check cables terminals | Semi-annual | necessary
Power Generation | LV Switchboard | AUX Switchboard | General cleaning | Semi-annual | necessary
Power Generation | Cables | DC Cables | Integrity inspection | Semi-annual | necessary
Power Generation | Cables | DC Cables | Cables visual inspection | Annual | necessary
Power Generation | Cables | DC Cables | Labelling and identification | Annual | necessary
Power Generation | Cables | AC Cables | Cables visual inspection | Semi-annual | necessary
Power Generation | Cables | AC Cables | Labelling and identification | Annual | necessary
Power Generation | Cables | AC Cables | Measurements inspection | Semi-annual | necessary
Power Generation | Inverters | Central Inverters | Safety equipment inspection | Annual | necessary
Power Generation | Inverters | Central Inverters | Integrity inspection | Semi-annual | necessary
Power Generation | Inverters | Central Inverters | Documents inspection | Semi-annual | necessary
Power Generation | Inverters | Central Inverters | Cables visual inspection | Annual | necessary
Power Generation | Inverters | Central Inverters | Labelling and identification | Annual | necessary
Power Generation | Inverters | Central Inverters | Electrical protections visual inspection | Semi-annual | necessary
Power Generation | Inverters | Central Inverters | Thermography inspection | Annual | necessary
Power Generation | Inverters | Central Inverters | Sensors functional verification | Annual | necessary
Power Generation | Inverters | Central Inverters | Measurements inspection | Annual | necessary
Power Generation | Inverters | Central Inverters | Parameters check | Semi-annual | necessary
Power Generation | Inverters | Central Inverters | Electrical protection correct operation | Semi-annual | necessary
Power Generation | Inverters | Central Inverters | Check ventilation system operation | Annual | necessary
Power Generation | Inverters | Central Inverters | Check fuse status | Annual | necessary
Power Generation | Inverters | Central Inverters | Check cables terminals | Semi-annual | necessary
Power Generation | Inverters | Central Inverters | Battery replacement | Every five years | According to manufacturers recomendations
Power Generation | Inverters | Central Inverters | Fans replacement | Every five years | According to manufacturers recomendations
Power Generation | Inverters | Central Inverters | General cleaning | Semi-annual | necessary
Power Generation | Inverters | Central Inverters | Ventilation cleaning | Annual | necessary
Power Generation | Inverters | String Inverters | Safety equipment inspection | Semi-annual | necessary
Power Generation | Inverters | String Inverters | Integrity inspection | Semi-annual | necessary
Power Generation | Inverters | String Inverters | Cables visual inspection | Annual | necessary
Power Generation | Inverters | String Inverters | Labelling and identification | Semi-annual | necessary
Power Generation | Inverters | String Inverters | Electrical protections visual inspection | Semi-annual | necessary
Power Generation | Inverters | String Inverters | Thermography inspection | Annual | necessary
Power Generation | Inverters | String Inverters | Measurements inspection | Semi-annual | necessary
Power Generation | Inverters | String Inverters | Parameters check | Annual | necessary
Power Generation | Inverters | String Inverters | Electrical protection correct operation | Annual | necessary
Power Generation | Inverters | String Inverters | Check ventilation system operation | Semi-annual | necessary
Power Generation | Inverters | String Inverters | Check cables terminals | Annual | necessary
Power Generation | Inverters | String Inverters | Battery replacement | Every five years | According to manufacturers recomendations
Power Generation | Inverters | String Inverters | Fans replacement | Every five years | According to manufacturers recomendations
Power Generation | Inverters | String Inverters | General cleaning | Annual | necessary
Power Generation | Inverters | String Inverters | Ventilation cleaning | Semi-annual | necessary
HV Systems | Cables | HV Cables | Cables visual inspection | Semi-annual | necessary
HV Systems | Cables | HV Cables | Labelling and identification | Semi-annual | necessary
HV Systems | Power Transformer |  | Integrity inspection | Semi-annual | necessary
HV Systems | Power Transformer |  | Cables visual inspection | Annual | necessary
HV Systems | Power Transformer |  | Mechanical visual inspection | Annual | necessary
HV Systems | Power Transformer |  | Labelling and identification | Annual | necessary
HV Systems | Power Transformer |  | Thermography inspection | Semi-annual | necessary
HV Systems | Power Transformer |  | Sensors functional verification | Semi-annual | necessary
HV Systems | Power Transformer |  | Measurements inspection | Semi-annual | necessary
HV Systems | Power Transformer |  | Parameters check | Annual | necessary
HV Systems | Power Transformer |  | Check correct operation | Semi-annual | necessary
HV Systems | Power Transformer |  | Check cables terminals | Semi-annual | necessary
HV Systems | Power Transformer |  | Power transformer cleaning | Semi-annual | necessary
HV Systems | HV Switchgear |  | Integrity inspection | Annual | necessary
HV Systems | HV Switchgear |  | Cables visual inspection | Annual | necessary
HV Systems | HV Switchgear |  | Mechanical visual inspection | Semi-annual | necessary
HV Systems | HV Switchgear |  | Labelling and identification | Annual | necessary
HV Systems | HV Switchgear |  | Electrical protections visual inspection | Semi-annual | necessary
HV Systems | HV Switchgear |  | Thermography inspection | Semi-annual | necessary
HV Systems | HV Switchgear |  | Sensors functional verification | Annual | necessary
HV Systems | HV Switchgear |  | Measurements inspection | Annual | necessary
HV Systems | HV Switchgear |  | Check correct operation | Annual | necessary
HV Systems | HV Switchgear |  | Check fuse status | Annual | necessary
HV Systems | HV Switchgear |  | Check cables terminals | Semi-annual | necessary
HV Systems | HV Switchgear |  | General cleaning | Annual | necessary
HV Systems | HV Switchgear |  | Mechanical lubrication | Semi-annual | necessary
HV Systems | Main Switchboard | Main AUX Switchboard | Integrity inspection | Annual | necessary
HV Systems | Main Switchboard | Main AUX Switchboard | Documents inspection | Annual | necessary
HV Systems | Main Switchboard | Main AUX Switchboard | Cables visual inspection | Annual | necessary
HV Systems | Main Switchboard | Main AUX Switchboard | Labelling and identification | Annual | necessary
HV Systems | Main Switchboard | Main AUX Switchboard | Electrical protections visual inspection | Annual | necessary
HV Systems | Main Switchboard | Main AUX Switchboard | Thermography inspection | Annual | necessary
HV Systems | Main Switchboard | Main AUX Switchboard | Sensors functional verification | Semi-annual | necessary
HV Systems | Main Switchboard | Main AUX Switchboard | Measurements inspection | Semi-annual | necessary
HV Systems | Main Switchboard | Main AUX Switchboard | Parameters check | Annual | necessary
HV Systems | Main Switchboard | Main AUX Switchboard | Check correct operation | Semi-annual | necessary
HV Systems | Main Switchboard | Main AUX Switchboard | Electrical protection correct operation | Annual | necessary
HV Systems | Main Switchboard | Main AUX Switchboard | Check fuse status | Annual | necessary
HV Systems | Main Switchboard | Main AUX Switchboard | Software maintenance | Annual | necessary
HV Systems | Main Switchboard | Main AUX Switchboard | Monitoring operation test | Annual | necessary
HV Systems | Main Switchboard | Main AUX Switchboard | Check cables terminals | Annual | necessary
HV Systems | Main Switchboard | Main AUX Switchboard | Battery replacement | Every five years | According to manufacturers recomendations
HV Systems | Main Switchboard | Main AUX Switchboard | General cleaning | Annual | necessary
HV Systems | Main Switchboard | Main AC Switchboard | Integrity inspection | Annual | necessary
HV Systems | Main Switchboard | Main AC Switchboard | Documents inspection | Semi-annual | necessary
HV Systems | Main Switchboard | Main AC Switchboard | Cables visual inspection | Annual | necessary
HV Systems | Main Switchboard | Main AC Switchboard | Labelling and identification | Annual | necessary
HV Systems | Main Switchboard | Main AC Switchboard | Electrical protections visual inspection | Annual | necessary
HV Systems | Main Switchboard | Main AC Switchboard | Thermography inspection | Semi-annual | necessary
HV Systems | Main Switchboard | Main AC Switchboard | Sensors functional verification | Annual | necessary
HV Systems | Main Switchboard | Main AC Switchboard | Measurements inspection | Annual | necessary
HV Systems | Main Switchboard | Main AC Switchboard | Check correct operation | Annual | necessary
HV Systems | Main Switchboard | Main AC Switchboard | Electrical protection correct operation | Annual | necessary
HV Systems | Main Switchboard | Main AC Switchboard | Check fuse status | Annual | necessary
HV Systems | Main Switchboard | Main AC Switchboard | Check cables terminals | Semi-annual | necessary
HV Systems | Main Switchboard | Main AC Switchboard | General cleaning | Annual | necessary
HV Systems | Power Monitoring | Power Analyser | Battery replacement | Every five years | According to manufacturers recomendations
HV Systems | Power Monitoring | Power Analyser | Cables visual inspection | Annual | necessary
HV Systems | Power Monitoring | Power Analyser | Labelling and identification | Annual | necessary
HV Systems | Power Monitoring | Power Analyser | Measurements inspection | Annual | necessary
HV Systems | Power Monitoring | Power Analyser | Integrity inspection | Annual | necessary
HV Systems | Power Monitoring | Power Analyser | Software maintenance | Annual | necessary
HV Systems | Power Monitoring | Power Analyser | Monitoring operation test | Semi-annual | necessary
HV Systems | Power Monitoring | Power Analyser | Parameters check | Semi-annual | necessary
HV Systems | Power Monitoring | Power Analyser | General cleaning | Semi-annual | necessary
HV Systems | Power Monitoring | Energy Meter | General cleaning | Annual | necessary
HV Systems | Power Monitoring | Energy Meter | Cables visual inspection | Annual | necessary
HV Systems | Power Monitoring | Energy Meter | Labelling and identification | Annual | necessary
HV Systems | Power Monitoring | Energy Meter | Measurements inspection | Annual | necessary
HV Systems | Power Monitoring | Energy Meter | Integrity inspection | Annual | necessary
HV Systems | Power Monitoring | Energy Meter | Monitoring operation test | Annual | necessary
HV Systems | Power Monitoring | Energy Meter | Parameters check | Annual | necessary
HV Systems | Power Monitoring | Energy Meter | Check cables terminals | Annual | necessary
HV Systems | Power Monitoring | Multifunctional HV Protection | Battery replacement | Every five years | According to manufacturers recomendations
HV Systems | Power Monitoring | Multifunctional HV Protection | Parameters check | Annual | necessary
HV Systems | Power Monitoring | Multifunctional HV Protection | Cables visual inspection | Annual | necessary
HV Systems | Power Monitoring | Multifunctional HV Protection | Labelling and identification | Annual | necessary
HV Systems | Power Monitoring | Multifunctional HV Protection | Integrity inspection | Annual | necessary
HV Systems | Power Monitoring | Multifunctional HV Protection | Software maintenance | Annual | necessary
HV Systems | Power Monitoring | Multifunctional HV Protection | Monitoring operation test | Annual | necessary
HV Systems | Power Monitoring | Multifunctional HV Protection | General cleaning | Annual | necessary
HV Systems | Power Monitoring | Power Control Unit | Battery replacement | Every five years | According to manufacturers recomendations
HV Systems | Power Monitoring | Power Control Unit | Electrical protection correct operation | Semi-annual | necessary
HV Systems | Power Monitoring | Power Control Unit | Battery inspection | Annual | necessary
HV Systems | Power Monitoring | Power Control Unit | Cables visual inspection | Semi-annual | necessary
HV Systems | Power Monitoring | Power Control Unit | Labelling and identification | Semi-annual | necessary
HV Systems | Power Monitoring | Power Control Unit | Sensors functional verification | Semi-annual | necessary
HV Systems | Power Monitoring | Power Control Unit | Integrity inspection | Semi-annual | necessary
HV Systems | Power Monitoring | Power Control Unit | Check correct operation | Semi-annual | necessary
HV Systems | Power Monitoring | Power Control Unit | Software maintenance | Semi-annual | necessary
HV Systems | Power Monitoring | Power Control Unit | Electrical protections visual inspection | Semi-annual | necessary
HV Systems | Power Monitoring | Power Control Unit | Monitoring operation test | Semi-annual | necessary
HV Systems | Power Monitoring | Power Control Unit | Check cables terminals | Semi-annual | necessary
HV Systems | Power Monitoring | Power Control Unit | Parameters check | Semi-annual | necessary
HV Systems | Power Monitoring | Power Control Unit | Measurements inspection | Annual | necessary
HV Systems | Power Monitoring | Power Control Unit | General cleaning | Annual | necessary
General Utilities | Backup Power Supply | UPS | Integrity inspection | Annual | necessary
General Utilities | Backup Power Supply | UPS | Cables visual inspection | Annual | necessary
General Utilities | Backup Power Supply | UPS | Thermography inspection | Annual | necessary
General Utilities | Backup Power Supply | UPS | Electrical protection correct operation | Annual | necessary
General Utilities | Backup Power Supply | UPS | Battery inspection | Annual | necessary
General Utilities | Backup Power Supply | UPS | Check ventilation system operation | Annual | necessary
General Utilities | Backup Power Supply | UPS | Check cables terminals | Annual | necessary
General Utilities | Backup Power Supply | UPS | General cleaning | Semi-annual | necessary
General Utilities | Backup Power Supply | Emergency Generator | Integrity inspection | Semi-annual | necessary
General Utilities | Backup Power Supply | Emergency Generator | Mechanical visual inspection | Annual | necessary
General Utilities | Backup Power Supply | Emergency Generator | Measurements inspection | Annual | necessary
General Utilities | Backup Power Supply | Emergency Generator | Parameters check | Annual | necessary
General Utilities | Backup Power Supply | Emergency Generator | Check correct operation | Annual | necessary
General Utilities | Backup Power Supply | Emergency Generator | Electrical protection correct operation | Semi-annual | necessary
General Utilities | Backup Power Supply | Emergency Generator | Battery inspection | Semi-annual | necessary
General Utilities | Backup Power Supply | Emergency Generator | Mechanical verification | Semi-annual | necessary
General Utilities | Backup Power Supply | Emergency Generator | Retightening | Annual | necessary
General Utilities | Backup Power Supply | Emergency Generator | Filters replacement | Every five years | According to manufacturers recomendations
General Utilities | General Utilities Switchboard |  | Integrity inspection | Semi-annual | necessary
General Utilities | General Utilities Switchboard |  | Documents inspection | Semi-annual | necessary
General Utilities | General Utilities Switchboard |  | Cables visual inspection | Semi-annual | necessary
General Utilities | General Utilities Switchboard |  | Labelling and identification | Semi-annual | necessary
General Utilities | General Utilities Switchboard |  | Thermography inspection | Annual | necessary
General Utilities | General Utilities Switchboard |  | Measurements inspection | Semi-annual | necessary
General Utilities | General Utilities Switchboard |  | Electrical protection correct operation | Semi-annual | necessary
General Utilities | General Utilities Switchboard |  | Check cables terminals | Annual | necessary
General Utilities | General Utilities Switchboard |  | General cleaning | Semi-annual | necessary
General Utilities | Auxiliary System | Lights and Electric Sockets | Integrity inspection | Annual | necessary
General Utilities | Auxiliary System | Lights and Electric Sockets | Cables visual inspection | Annual | necessary
General Utilities | Auxiliary System | Lights and Electric Sockets | Measurements inspection | Semi-annual | necessary
General Utilities | Auxiliary System | Lights and Electric Sockets | Check correct operation | Annual | necessary
General Utilities | Auxiliary System | Lights and Electric Sockets | General cleaning | Semi-annual | necessary
General Utilities | Auxiliary System | HVAC | Air conditioning visual inspection | Semi-annual | necessary
General Utilities | Auxiliary System | HVAC | Heater visual inspection | Semi-annual | necessary
General Utilities | Auxiliary System | HVAC | Ventilation visual inspection | Semi-annual | necessary
General Utilities | Auxiliary System | HVAC | Sensors functional verification | Semi-annual | necessary
General Utilities | Auxiliary System | HVAC | Measurements inspection | Semi-annual | necessary
General Utilities | Auxiliary System | HVAC | Check correct operation | Semi-annual | necessary
General Utilities | Auxiliary System | HVAC | Check ventilation system operation | Semi-annual | necessary
General Utilities | Auxiliary System | HVAC | Air conditioning cleaning | Semi-annual | necessary
General Utilities | Auxiliary System | HVAC | Ventilation cleaning | Semi-annual | necessary
General Utilities | Auxiliary System | HVAC | Heater cleaning | Semi-annual | necessary
General Utilities | Water Supply System |  | Integrity inspection | Annual | necessary
General Utilities | Fire Detection Central |  | Sensors functional verification | Semi-annual | necessary
General Utilities | Fire Detection Central |  | Check correct operation | Semi-annual | necessary
General Utilities | Fire Detection Central |  | Electrical protection correct operation | Semi-annual | necessary
General Utilities | Fire Detection Central |  | Battery inspection | Semi-annual | necessary
General Utilities | Fire Detection Central |  | General cleaning | Annual | necessary
General Utilities | Fire Detection Central |  | Cameras & Sensors cleaning | Semi-annual | necessary
General Utilities | Lightning Protection |  | Integrity inspection | Annual | necessary
General Utilities | Low Voltage Power Transformer |  | Integrity inspection | Semi-annual | necessary
General Utilities | Low Voltage Power Transformer |  | Cables visual inspection | Semi-annual | necessary
General Utilities | Low Voltage Power Transformer |  | Mechanical visual inspection | Semi-annual | necessary
General Utilities | Low Voltage Power Transformer |  | Labelling and identification | Annual | necessary
General Utilities | Low Voltage Power Transformer |  | Thermography inspection | Annual | necessary
General Utilities | Low Voltage Power Transformer |  | Sensors functional verification | Semi-annual | necessary
General Utilities | Low Voltage Power Transformer |  | Measurements inspection | Semi-annual | necessary
General Utilities | Low Voltage Power Transformer |  | Parameters check | Semi-annual | necessary
General Utilities | Low Voltage Power Transformer |  | Check correct operation | Semi-annual | necessary
General Utilities | Low Voltage Power Transformer |  | Check cables terminals | Semi-annual | necessary
General Utilities | Low Voltage Power Transformer |  | Power transformer cleaning | Semi-annual | necessary
Infrastructure | Field | Fence | Integrity inspection | Annual | necessary
Infrastructure | Field | Fence | Mechanical lubrication | Annual | necessary
Infrastructure | Field | Vegetation | Vegetation clearing | Semi-annual | necessary
Infrastructure | Field | Paths | Integrity inspection | Semi-annual | necessary
Infrastructure | Field | Paths | Vegetation clearing | Semi-annual | necessary
Infrastructure | Field | Drainage System | General cleaning | Annual | necessary
Infrastructure | Field | Manholes | Integrity inspection | Semi-annual | necessary
Infrastructure | Buildings |  | Integrity inspection | Annual | necessary
Infrastructure | Buildings |  | Documents inspection | Annual | necessary
Infrastructure | Buildings |  | General cleaning | Annual | necessary
Infrastructure | Safety |  | Safety equipment inspection | Annual | necessary
Infrastructure | Safety |  | Check correct operation | Semi-annual | necessary
Infrastructure | PV Support Structure | Fixed Structure | Integrity inspection | Semi-annual | necessary
Infrastructure | PV Support Structure | Fixed Structure | Retightening | Semi-annual | necessary
Infrastructure | PV Support Structure | Solar Tracker | Integrity inspection | Annual | necessary
Infrastructure | PV Support Structure | Solar Tracker | Cables visual inspection | Semi-annual | necessary
Infrastructure | PV Support Structure | Solar Tracker | Mechanical visual inspection | Semi-annual | necessary
Infrastructure | PV Support Structure | Solar Tracker | Labelling and identification | Annual | necessary
Infrastructure | PV Support Structure | Solar Tracker | Thermography inspection | Annual | necessary
Infrastructure | PV Support Structure | Solar Tracker | Measurements inspection | Semi-annual | necessary
Infrastructure | PV Support Structure | Solar Tracker | Parameters check | Semi-annual | necessary
Infrastructure | PV Support Structure | Solar Tracker | Check correct operation | Annual | necessary
Infrastructure | PV Support Structure | Solar Tracker | Electrical protection correct operation | Semi-annual | necessary
Infrastructure | PV Support Structure | Solar Tracker | Monitoring operation test | Annual | necessary
Infrastructure | PV Support Structure | Solar Tracker | Check cables terminals | Semi-annual | necessary
Infrastructure | PV Support Structure | Solar Tracker | Retightening | Semi-annual | necessary
Infrastructure | PV Support Structure | Solar Tracker | Battery replacement | Every five years | According to manufacturers recomendations
Infrastructure | PV Support Structure | Solar Tracker | General cleaning | Semi-annual | necessary
Infrastructure | PV Support Structure | Solar Tracker | Mechanical lubrication | Annual | necessary
Monitoring System | Weather Station |  | Integrity inspection | Annual | necessary
Monitoring System | Weather Station |  | Cables visual inspection | Annual | necessary
Monitoring System | Weather Station |  | Sensors functional verification | Annual | necessary
Monitoring System | Weather Station |  | Measurements inspection | Annual | necessary
Monitoring System | Weather Station |  | Check correct operation | Semi-annual | necessary
Monitoring System | Weather Station |  | Electrical protection correct operation | Annual | necessary
Monitoring System | Weather Station |  | Battery inspection | Annual | necessary
Monitoring System | Weather Station |  | Monitoring operation test | Semi-annual | necessary
Monitoring System | Weather Station |  | General cleaning | Annual | necessary
Monitoring System | Weather Station |  | Cameras & Sensors cleaning | Annual | necessary
Monitoring System | Weather Station | Irradiation Sensors | Integrity inspection | Annual | necessary
Monitoring System | Weather Station | Irradiation Sensors | Cables visual inspection | Semi-annual | necessary
Monitoring System | Weather Station | Irradiation Sensors | Sensors functional verification | Semi-annual | necessary
Monitoring System | Weather Station | Irradiation Sensors | Sensors calibration | Annual | necessary
Monitoring System | Weather Station | Irradiation Sensors | Cameras & Sensors cleaning | Annual | necessary
Monitoring System | Monitoring System Cabling |  | Cables visual inspection | Semi-annual | necessary
Monitoring System | Monitoring System Cabling |  | Labelling and identification | Semi-annual | necessary
Monitoring System | Monitoring System Cabling |  | Monitoring operation test | Semi-annual | necessary
Monitoring System | Communication Board |  | Integrity inspection | Annual | necessary
Monitoring System | Communication Board |  | Documents inspection | Annual | necessary
Monitoring System | Communication Board |  | Cables visual inspection | Annual | necessary
Monitoring System | Communication Board |  | Electrical protection correct operation | Annual | necessary
Monitoring System | Communication Board |  | Battery inspection | Annual | necessary
Monitoring System | Communication Board |  | Check ventilation system operation | Annual | necessary
Monitoring System | Communication Board |  | Monitoring operation test | Annual | necessary
Monitoring System | Communication Board |  | Check cables terminals | Annual | necessary
Monitoring System | Communication Board |  | General cleaning | Annual | necessary
Monitoring System | Communication Board |  | Ventilation cleaning | Annual | necessary
Monitoring System | Monitoring System Software |  | Measurements inspection | Annual | necessary
Monitoring System | Monitoring System Software |  | Software maintenance | Monthly | necessary
Monitoring System | Monitoring System Software |  | Monitoring operation test | Annual | necessary
Monitoring System | Data Logger |  | Integrity inspection | Semi-annual | necessary
Monitoring System | Data Logger |  | Check correct operation | Semi-annual | necessary
Monitoring System | Data Logger |  | Monitoring operation test | Semi-annual | necessary
Security System | Security System Central |  | Parameters check | Semi-annual | necessary
Security System | Security System Central |  | Check correct operation | Semi-annual | necessary
Security System | Security System Central |  | Battery inspection | Annual | necessary
Security System | Security System Central |  | Check ventilation system operation | Semi-annual | necessary
Security System | Security System Central |  | General cleaning | Annual | necessary
Security System | System CCTV |  | Integrity inspection | Annual | necessary
Security System | System CCTV |  | Sensors functional verification | Annual | necessary
Security System | System CCTV |  | Cameras & Sensors cleaning | Annual | necessary
Security System | Intrusion Systems |  | Integrity inspection | Annual | necessary
Security System | Intrusion Systems |  | Sensors functional verification | Semi-annual | necessary
Security System | Intrusion Systems |  | Cameras & Sensors cleaning | Annual | necessary
Security System | Security System Cabling |  | Cables visual inspection | Semi-annual | necessary
Security System | Security System Cabling |  | Labelling and identification | Semi-annual | necessary
Security System | Security System Board |  | Integrity inspection | Annual | necessary
Security System | Security System Board |  | Documents inspection | Semi-annual | necessary
Security System | Security System Board |  | Cables visual inspection | Semi-annual | necessary
Security System | Security System Board |  | Electrical protection correct operation | Semi-annual | necessary
Security System | Security System Board |  | Battery inspection | Semi-annual | necessary
Security System | Security System Board |  | Monitoring operation test | Annual | necessary
Security System | Security System Board |  | Check cables terminals | Semi-annual | necessary
Security System | Security System Board |  | General cleaning | Annual | necessary
Security System | Security System Board |  | Ventilation cleaning | Annual | necessary
Spare parts |  |  | Inventory of stock | Annual | necessary | e.g. Monthly
Spare parts |  |  | Visual inspection of stock conditions | Quarterly | necessary
Spare parts |  |  | Stock replenishment | Ongoing | necessary
Spare parts |  |  | Review failure rates and adjust stock keeping | Annual | necessary | e.g. Monthly